## Equations
ComfStand |  | CAT | ComfMod | PMV-based model when adaptive is not applicable | Season / Climate zone | Cooling setpoint temperature (°C) |  |  | Heating setpoint temperature (°C) |  |  |  | PMOT(7DRM) or RMOT(30DRM) | Adaptive Comfort Eq | PMV-based Comf Eq Cooling |  |  | PMV-based Comf Eq Heating |  |  | CST |  |  |  | HST
[6 empty] | WMOT < ACSTall | ACSTall < WMOT < ACSTaul | ACSTaul < WMOT | WMOT < AHSTall | AHSTall < WMOT < AHSTaul | AHSTaul < WMOT | implemented in accim? |  |  | WMOT < ACSTall | ACSTaul < WMOT | Offset | WMOT < ACSTall | ACSTaul < WMOT | Offset | Comf Eq | Upper App Limit | Lower App Limit | Offset | Comf Eq | Upper App Limit | Lower App Limit | Offset
0 | CTE | NA | NA |  |  | 23:00-08:00h: 27 / 08:00-23:00h: 25 |  |  | 23:00-08:00h: 17 / 08:00-23:00h: 20 |  |  | YES
1 | INT EN16798-1 | 1 | 0 |  | SS | 25.5 |  |  | 23.5 |  |  | YES | [9 empty] | 30 | 10 | 2 |  | 30 | 10 | -3
[5 empty] | WS | 25 |  |  | 21 |  |  | YES | [9 empty] | 30 | 10 | 2 |  | 30 | 10 | -3
|  |  | 1 | Spanish Building Code | All | 27-25 | RMOT*0.33+18.8+2 | 27-25 | 17-20 | RMOT*0.33+18.8-3 | 17-20 | YES | RMOT | 0.33+18.8 | [7 empty] | 30 | 10 | 2 |  | 30 | 10 | -3
|  |  | 2 | EN16798-1 Static | All | 25 | RMOT*0.33+18.8+2 | 25.5 | 21 | RMOT*0.33+18.8-3 | 23.5 | YES | RMOT | 0.33+18.8 | [7 empty] | 30 | 10 | 2 |  | 30 | 10 | -3
|  |  | 3 | Adap. Limits Horizont. Extended | All | 10*0.33+18.8+2 | RMOT*0.33+18.8+2 | 30*0.33+18.8+2 | 10*0.33+18.8-3 | RMOT*0.33+18.8-3 | 30*0.33+18.8-3 | YES | RMOT | 0.33+18.8 | [7 empty] | 30 | 10 | 2 |  | 30 | 10 | -3
|  | 2 | 0 |  | SS | 26 |  |  | 23 |  |  | YES | [9 empty] | 30 | 10 | 3 |  | 30 | 10 | -4
[5 empty] | WS | 25 |  |  | 20 |  |  | YES | [9 empty] | 30 | 10 | 3 |  | 30 | 10 | -4
|  |  | 1 | Spanish Building Code | All | 27-25 | RMOT*0.33+18.8+3 | 27-25 | 17-20 | RMOT*0.33+18.8-4 | 17-20 | YES | RMOT | 0.33+18.8 | [7 empty] | 30 | 10 | 3 |  | 30 | 10 | -4
|  |  | 2 | EN16798-1 Static | All | 25 | RMOT*0.33+18.8+3 | 26 | 20 | RMOT*0.33+18.8-4 | 23 | YES | RMOT | 0.33+18.8 | [7 empty] | 30 | 10 | 3 |  | 30 | 10 | -4
|  |  | 3 | Adap. Limits Horizont. Extended | All | 10*0.33+18.8+3 | RMOT*0.33+18.8+3 | 30*0.33+18.8+3 | 10*0.33+18.8-4 | RMOT*0.33+18.8-4 | 30*0.33+18.8-4 | YES | RMOT | 0.33+18.8 | [7 empty] | 30 | 10 | 3 |  | 30 | 10 | -4
|  | 3 | 0 |  | SS | 27 |  |  | 22 |  |  | YES | [9 empty] | 30 | 10 | 4 |  | 30 | 10 | -5
[5 empty] | WS | 25 |  |  | 18 |  |  | YES | [9 empty] | 30 | 10 | 4 |  | 30 | 10 | -5
|  |  | 1 | Spanish Building Code | All | 27-25 | RMOT*0.33+18.8+4 | 27-25 | 17-20 | RMOT*0.33+18.8-5 | 17-20 | YES | RMOT | 0.33+18.8 | [7 empty] | 30 | 10 | 4 |  | 30 | 10 | -5
|  |  | 2 | EN16798-1 Static | All | 25 | RMOT*0.33+18.8+4 | 27 | 18 | RMOT*0.33+18.8-5 | 22 | YES | RMOT | 0.33+18.8 | [7 empty] | 30 | 10 | 4 |  | 30 | 10 | -5
|  |  | 3 | Adap. Limits Horizont. Extended | All | 10*0.33+18.8+4 | RMOT*0.33+18.8+4 | 30*0.33+18.8+4 | 10*0.33+18.8-5 | RMOT*0.33+18.8-5 | 30*0.33+18.8-5 | YES | RMOT | 0.33+18.8 | [7 empty] | 30 | 10 | 4 |  | 30 | 10 | -5
2 | INT ASHRAE55 | 80 | 0 |  | SS | 27 |  |  | 22 |  |  | YES | PMOT | 0.31+17.8 | [7 empty] | 33.5 | 10 | 3.5 |  | 33.5 | 10 | -3.5
[5 empty] | WS | 25 |  |  | 19 |  |  | YES | PMOT | 0.31+17.8 | [7 empty] | 33.5 | 10 | 3.5 |  | 33.5 | 10 | -3.5
|  |  | 1 | CTE | All | 27-25 | PMOT*0.31+17.8+3.5 | 27-25 | 17-20 | PMOT*0.31+17.8-3.5 | 17-20 | YES | PMOT | 0.31+17.8 | [7 empty] | 33.5 | 10 | 3.5 |  | 33.5 | 10 | -3.5
|  |  | 2 | ISO 7730 | All | 25 | PMOT*0.31+17.8+3.5 | 27 | 19 | PMOT*0.31+17.8-3.5 | 22 | YES | PMOT | 0.31+17.8 | [7 empty] | 33.5 | 10 | 3.5 |  | 33.5 | 10 | -3.5
|  |  | 3 | Adap. Limits Horizont. Extended | All | 10*0.31+17.8+3.5 | PMOT*0.31+17.8+3.5 | 33.5*0.31+17.8+3.5 | 10*0.31+17.8-3.5 | PMOT*0.31+17.8-3.5 | 33.5*0.31+17.8-3.5 | YES | PMOT | 0.31+17.8 | [7 empty] | 33.5 | 10 | 3.5 |  | 33.5 | 10 | -3.5
|  | 90 | 0 |  | SS | 26 |  |  | 23 |  |  | YES | PMOT | 0.31+17.8 | [7 empty] | 33.5 | 10 | 2.5 |  | 33.5 | 10 | -2.5
[5 empty] | WS | 24 |  |  | 20 |  |  | YES | PMOT | 0.31+17.8 | [7 empty] | 33.5 | 10 | 2.5 |  | 33.5 | 10 | -2.5
|  |  | 1 | CTE | All | 27-25 | PMOT*0.31+17.8+2.5 | 27-25 | 17-20 | PMOT*0.31+17.8-2.5 | 17-20 | YES | PMOT | 0.31+17.8 | [7 empty] | 33.5 | 10 | 2.5 |  | 33.5 | 10 | -2.5
|  |  | 2 | ISO 7730 | All | 24 | PMOT*0.31+17.8+2.5 | 26 | 20 | PMOT*0.31+17.8-2.5 | 23 | YES | PMOT | 0.31+17.8 | [7 empty] | 33.5 | 10 | 2.5 |  | 33.5 | 10 | -2.5
|  |  | 3 | Adap. Limits Horizont. Extended | All | 10*0.31+17.8+2.5 | PMOT*0.31+17.8+2.5 | 33.5*0.31+17.8+2.5 | 10*0.31+17.8-2.5 | PMOT*0.31+17.8-2.5 | 33.5*0.31+17.8-2.5 | YES | PMOT | 0.31+17.8 | [7 empty] | 33.5 | 10 | 2.5 |  | 33.5 | 10 | -2.5
3 | JPN Rijal | 80 | 0 |  | All | 28 |  |  | 18 |  |  | YES | PMOT | 0.48+14.4 | [7 empty] | 30 | 5 | 3.5 |  | 30 | 5 | -3.5
|  |  | 1 | COOLBIZ | All | 28 | PMOT*0.48+14.4+3.5 | 28 | 18 | PMOT*0.48+14.4-3.5 | 18 | YES | PMOT | 0.48+14.4 | [7 empty] | 30 | 5 | 3.5 |  | 30 | 5 | -3.5
|  |  | 2 | ISO 7730 | All | 25 | PMOT*0.48+14.4+3.5 | 27 | 19 | PMOT*0.48+14.4-3.5 | 22 | YES | PMOT | 0.48+14.4 | [7 empty] | 30 | 5 | 3.5 |  | 30 | 5 | -3.5
|  |  | 3 | Adap. Limits Horizont. Extended | All | 5*0.48+14.4+3.5 | PMOT*0.48+14.4+3.5 | 30*0.48+14.4+3.5 | 5*0.48+14.4-3.5 | PMOT*0.48+14.4-3.5 | 30*0.48+14.4-3.5 | YES | PMOT | 0.48+14.4 | [7 empty] | 30 | 5 | 3.5 |  | 30 | 5 | -3.5
|  | 90 | 0 |  | All | 27 |  |  | 19 |  |  | YES | PMOT | 0.48+14.4 | [7 empty] | 30 | 5 | 2.5 |  | 30 | 5 | -2.5
|  |  | 1 | COOLBIZ | All | 27 | PMOT*0.48+14.4+2.5 | 27 | 19 | PMOT*0.48+14.4-2.5 | 19 | YES | PMOT | 0.48+14.4 | [7 empty] | 30 | 5 | 2.5 |  | 30 | 5 | -2.5
|  |  | 2 | ISO 7730 | All | 24 | PMOT*0.48+14.4+2.5 | 26 | 20 | PMOT*0.48+14.4-2.5 | 23 | YES | PMOT | 0.48+14.4 | [7 empty] | 30 | 5 | 2.5 |  | 30 | 5 | -2.5
|  |  | 3 | Adap. Limits Horizont. Extended | All | 5*0.48+14.4+2.5 | PMOT*0.48+14.4+2.5 | 30*0.48+14.4+2.5 | 5*0.48+14.4-2.5 | PMOT*0.48+14.4-2.5 | 30*0.48+14.4-2.5 | YES | PMOT | 0.48+14.4 | [7 empty] | 30 | 5 | 2.5 |  | 30 | 5 | -2.5
4 | CHN GB/T 50785 - Cold | 1 (90%) | - | Adap. Limits Horizont. Extended | All | 18*0.77+12.04 | PMOT*0.77+12.04 | 28*0.77+12.04 | 18*0.87+2.76 | PMOT*0.87+2.76 | 28*0.87+2.76 | YES | [9 empty] | 28 | 18 |  |  | 28 | 18
|  | 2 (75-90%) | - | Adap. Limits Horizont. Extended | All | 18*0.73+15.28 | PMOT*0.73+15.28 | 30*0.73+15.28 | 16*0.91-0.48 | PMOT*0.91-0.48 | 28*0.91-0.48 | YES | [9 empty] | 30 | 18 |  |  | 28 | 16
5 | CHN GB/T 50785 - Hot & Mild | 1 (90%) | - | Adap. Limits Horizont. Extended | All | 18*0.77+9.34 | PMOT*0.77+9.34 | 28*0.77+9.34 | 18*0.87-0.31 | PMOT*0.87-0.31 | 28*0.87-0.31 | YES | [9 empty] | 28 | 18 |  |  | 28 | 18
|  | 2 (75-90%) | - | Adap. Limits Horizont. Extended | All | 18*0.73+12.72 | PMOT*0.73+12.72 | 30*0.73+12.72 | 16*0.91-3.69 | PMOT*0.91-3.69 | 28*0.91-3.69 | YES | [9 empty] | 30 | 18 |  |  | 28 | 16
6 | CHN Yang | 80 | 0 |  | All | ? |  |  | ? |  |  | NO | PMOT | [7 empty] | 0.30+25.9 | 30 | -7 |  | 0.32+14.88 | 30 | -7
|  |  | 1 |  | All | ? | ? | ? | ? | ? | ? | NO | PMOT | [7 empty] | 0.30+25.9 | 30 | -7 |  | 0.32+14.88 | 30 | -7
|  |  | 2 | ISO 7730 | All | 25 | PMOT*0.30+25.9 | 27 | 19 | PMOT*0.32+14.88 | 22 | YES | PMOT | [7 empty] | 0.30+25.9 | 30 | -7 |  | 0.32+14.88 | 30 | -7
|  |  | 3 | Adap. Limits Horizont. Extended | All | -7*0.30+25.9 | PMOT*0.30+25.9 | 30*0.30+25.9 | -7*0.32+14.88 | PMOT*0.32+14.88 | 30*0.32+14.88 | YES | PMOT | [7 empty] | 0.30+25.9 | 30 | -7 |  | 0.32+14.88 | 30 | -7
|  | 90 | 0 |  | All | ? |  |  | ? |  |  | NO | PMOT | [7 empty] | 0.30+23.6 | 30 | -7 |  | 0.31+17.14 | 30 | -7
|  |  | 1 |  | All | ? | ? | ? | ? | ? | ? | NO | PMOT | [7 empty] | 0.30+23.6 | 30 | -7 |  | 0.31+17.14 | 30 | -7
|  |  | 2 | ISO 7730 | All | 24 | PMOT*0.30+23.6 | 26 | 20 | PMOT*0.31+17.14 | 23 | YES | PMOT | [7 empty] | 0.30+23.6 | 30 | -7 |  | 0.31+17.14 | 30 | -7
|  |  | 3 | Adap. Limits Horizont. Extended | All | -7*0.30+23.6 | PMOT*0.30+23.6 | 30*0.30+23.6 | -7*0.31+17.14 | PMOT*0.31+17.14 | 30*0.31+17.14 | YES | PMOT | [7 empty] | 0.30+23.6 | 30 | -7 |  | 0.31+17.14 | 30 | -7
7 | IND IMAC C NV | 80 | 0 |  | All | PMOT*0.078+23.25+2.72 | PMOT*0.078+23.25+1 | PMOT*0.078+23.25+1 | PMOT*0.078+23.25-2.72 | PMOT*0.078+23.25-1 | PMOT*0.078+23.25-1 | YES | PMOT | 0.078+23.25 | 0.078+23.25 | 0.078+23.25 | 2.72 | 0.078+23.25 | 0.078+23.25 | -2.72 |  | 31 | 12.5 | 1 |  | 31 | 12.5 | -1
|  |  | 1 | Indian Building Code | All | PMOT*0.078+23.25+2.72 | PMOT*0.54+12.83+4.1 | PMOT*0.078+23.25+2.72 | PMOT*0.078+23.25-2.72 | PMOT*0.54+12.83-4.1 | PMOT*0.078+23.25-2.72 | YES | PMOT | 0.54+12.83 | 0.078+23.25 | 0.078+23.25 | 2.72 | 0.078+23.25 | 0.078+23.25 | -2.72 |  | 31 | 12.5 | 4.1 |  | 31 | 12.5 | -4.1
|  |  | 2 | ISO 7730 | All | 25 | PMOT*0.54+12.83+4.1 | 27 | 19 | PMOT*0.54+12.83-4.1 | 22 | YES | PMOT | 0.54+12.83 | 0.078+23.25 | 0.078+23.25 | 2.72 | 0.078+23.25 | 0.078+23.25 | -2.72 |  | 31 | 12.5 | 4.1 |  | 31 | 12.5 | -4.1
|  |  | 3 | Adap. Limits Horizont. Extended | All | 12.5*0.54+12.83+4.1 | PMOT*0.54+12.83+4.1 | 31*0.54+12.83+4.1 | 12.5*0.54+12.83-4.1 | PMOT*0.54+12.83-4.1 | 31*0.54+12.83-4.1 | YES | PMOT | 0.54+12.83 | 0.078+23.25 | 0.078+23.25 | 2.72 | 0.078+23.25 | 0.078+23.25 | -2.72 |  | 31 | 12.5 | 4.1 |  | 31 | 12.5 | -4.1
|  | 85 | 0 |  | All | PMOT*0.078+23.25+2.11 | PMOT*0.078+23.25+3.3 | PMOT*0.078+23.25+3.3 | PMOT*0.078+23.25-2.11 | PMOT*0.078+23.25-3.3 | PMOT*0.078+23.25-3.3 | YES | PMOT | 0.078+23.25 | 0.078+23.25 | 0.078+23.25 | 2.11 | 0.078+23.25 | 0.078+23.25 | -2.11 |  | 31 | 12.5 | 3.3 |  | 31 | 12.5 | -3.3
|  |  | 1 | Indian Building Code | All | PMOT*0.078+23.25+2.11 | PMOT*0.54+12.83+3.3 | PMOT*0.078+23.25+2.11 | PMOT*0.078+23.25-2.11 | PMOT*0.54+12.83-3.3 | PMOT*0.078+23.25-2.11 | YES | PMOT | 0.54+12.83 | 0.078+23.25 | 0.078+23.25 | 2.11 | 0.078+23.25 | 0.078+23.25 | -2.11 |  | 31 | 12.5 | 3.3 |  | 31 | 12.5 | -3.3
|  |  | 2 | ISO 7730 | All | 24.5 | PMOT*0.54+12.83+3.3 | 26.5 | 19.5 | PMOT*0.54+12.83-3.3 | 22.5 | YES | PMOT | 0.54+12.83 | 0.078+23.25 | 0.078+23.25 | 2.11 | 0.078+23.25 | 0.078+23.25 | -2.11 |  | 31 | 12.5 | 3.3 |  | 31 | 12.5 | -3.3
|  |  | 3 | Adap. Limits Horizont. Extended | All | 12.5*0.54+12.83+3.3 | PMOT*0.54+12.83+3.3 | 31*0.54+12.83+3.3 | 12.5*0.54+12.83-3.3 | PMOT*0.54+12.83-3.3 | 31*0.54+12.83-3.3 | YES | PMOT | 0.54+12.83 | 0.078+23.25 | 0.078+23.25 | 2.11 | 0.078+23.25 | 0.078+23.25 | -2.11 |  | 31 | 12.5 | 3.3 |  | 31 | 12.5 | -3.3
|  | 90 | 0 |  | All | PMOT*0.078+23.25+1.5 | PMOT*0.078+23.25+2.4 | PMOT*0.078+23.25+2.4 | PMOT*0.078+23.25-1.5 | PMOT*0.078+23.25-2.4 | PMOT*0.078+23.25-2.4 | YES | PMOT | 0.078+23.25 | 0.078+23.25 | 0.078+23.25 | 1.5 | 0.078+23.25 | 0.078+23.25 | -1.5 |  | 31 | 12.5 | 2.4 |  | 31 | 12.5 | -2.4
|  |  | 1 | Indian Building Code | All | PMOT*0.078+23.25+1.5 | PMOT*0.54+12.83+2.4 | PMOT*0.078+23.25+1.5 | PMOT*0.078+23.25-1.5 | PMOT*0.54+12.83-2.4 | PMOT*0.078+23.25-1.5 | YES | PMOT | 0.54+12.83 | 0.078+23.25 | 0.078+23.25 | 1.5 | 0.078+23.25 | 0.078+23.25 | -1.5 |  | 31 | 12.5 | 2.4 |  | 31 | 12.5 | -2.4
|  |  | 2 | ISO 7730 | All | 24 | PMOT*0.54+12.83+2.4 | 26 | 20 | PMOT*0.54+12.83-2.4 | 23 | YES | PMOT | 0.54+12.83 | 0.078+23.25 | 0.078+23.25 | 1.5 | 0.078+23.25 | 0.078+23.25 | -1.5 |  | 31 | 12.5 | 2.4 |  | 31 | 12.5 | -2.4
|  |  | 3 | Adap. Limits Horizont. Extended | All | 12.5*0.54+12.83+2.4 | PMOT*0.54+12.83+2.4 | 31*0.54+12.83+2.4 | 12.5*0.54+12.83-2.4 | PMOT*0.54+12.83-2.4 | 31*0.54+12.83-2.4 | YES | PMOT | 0.54+12.83 | 0.078+23.25 | 0.078+23.25 | 1.5 | 0.078+23.25 | 0.078+23.25 | -1.5 |  | 31 | 12.5 | 2.4 |  | 31 | 12.5 | -2.4
8 | IND IMAC C MM | 80 | 0 |  | All | PMOT*0.078+23.25+2.72 | PMOT*0.078+23.25+5.9 | PMOT*0.078+23.25+5.9 | PMOT*0.078+23.25-2.72 | PMOT*0.078+23.25-5.9 | PMOT*0.078+23.25-5.9 | YES | PMOT | 0.078+23.25 | 0.078+23.25 | 0.078+23.25 | 2.72 | 0.078+23.25 | 0.078+23.25 | -2.72 |  | 38.5 | 13 | 5.9 |  | 38.5 | 13 | -5.9
|  |  | 1 | Indian Building Code | All | PMOT*0.078+23.25+2.72 | PMOT*0.28+17.87+5.9 | PMOT*0.078+23.25+2.72 | PMOT*0.078+23.25-2.72 | PMOT*0.28+17.87-5.9 | PMOT*0.078+23.25-2.72 | YES | PMOT | 0.28+17.87 | 0.078+23.25 | 0.078+23.25 | 2.72 | 0.078+23.25 | 0.078+23.25 | -2.72 |  | 38.5 | 13 | 5.9 |  | 38.5 | 13 | -5.9
|  |  | 2 | ISO 7730 | All | 25 | PMOT*0.28+17.87+5.9 | 27 | 19 | PMOT*0.28+17.87-5.9 | 22 | YES | PMOT | 0.28+17.87 | 0.078+23.25 | 0.078+23.25 | 2.72 | 0.078+23.25 | 0.078+23.25 | -2.72 |  | 38.5 | 13 | 5.9 |  | 38.5 | 13 | -5.9
|  |  | 3 | Adap. Limits Horizont. Extended | All | 13*0.28+17.87+5.9 | PMOT*0.28+17.87+5.9 | 38.5*0.28+17.87+5.9 | 13*0.28+17.87-5.9 | PMOT*0.28+17.87-5.9 | 38.5*0.28+17.87-5.9 | YES | PMOT | 0.28+17.87 | 0.078+23.25 | 0.078+23.25 | 2.72 | 0.078+23.25 | 0.078+23.25 | -2.72 |  | 38.5 | 13 | 5.9 |  | 38.5 | 13 | -5.9
|  | 85 | 0 |  | All | PMOT*0.078+23.25+2.11 | PMOT*0.078+23.25+4.8 | PMOT*0.078+23.25+4.8 | PMOT*0.078+23.25-2.11 | PMOT*0.078+23.25-4.8 | PMOT*0.078+23.25-4.8 | YES | PMOT | 0.078+23.25 | 0.078+23.25 | 0.078+23.25 | 2.11 | 0.078+23.25 | 0.078+23.25 | -2.11 |  | 38.5 | 13 | 4.8 |  | 38.5 | 13 | -4.8
|  |  | 1 | Indian Building Code | All | PMOT*0.078+23.25+2.11 | PMOT*0.28+17.87+4.8 | PMOT*0.078+23.25+2.11 | PMOT*0.078+23.25-2.11 | PMOT*0.28+17.87-4.8 | PMOT*0.078+23.25-2.11 | YES | PMOT | 0.28+17.87 | 0.078+23.25 | 0.078+23.25 | 2.11 | 0.078+23.25 | 0.078+23.25 | -2.11 |  | 38.5 | 13 | 4.8 |  | 38.5 | 13 | -4.8
|  |  | 2 | ISO 7730 | All | 24.5 | PMOT*0.28+17.87+4.8 | 26.5 | 19.5 | PMOT*0.28+17.87-4.8 | 22.5 | YES | PMOT | 0.28+17.87 | 0.078+23.25 | 0.078+23.25 | 2.11 | 0.078+23.25 | 0.078+23.25 | -2.11 |  | 38.5 | 13 | 4.8 |  | 38.5 | 13 | -4.8
|  |  | 3 | Adap. Limits Horizont. Extended | All | 13*0.28+17.87+4.8 | PMOT*0.28+17.87+4.8 | 38.5*0.28+17.87+4.8 | 13*0.28+17.87-4.8 | PMOT*0.28+17.87-4.8 | 38.5*0.28+17.87-4.8 | YES | PMOT | 0.28+17.87 | 0.078+23.25 | 0.078+23.25 | 2.11 | 0.078+23.25 | 0.078+23.25 | -2.11 |  | 38.5 | 13 | 4.8 |  | 38.5 | 13 | -4.8
|  | 90 | 0 |  | All | PMOT*0.078+23.25+1.5 | PMOT*0.078+23.25+3.5 | PMOT*0.078+23.25+3.5 | PMOT*0.078+23.25-1.5 | PMOT*0.078+23.25-3.5 | PMOT*0.078+23.25-3.5 | YES | PMOT | 0.078+23.25 | 0.078+23.25 | 0.078+23.25 | 1.5 | 0.078+23.25 | 0.078+23.25 | -1.5 |  | 38.5 | 13 | 3.5 |  | 38.5 | 13 | -3.5
|  |  | 1 | Indian Building Code | All | PMOT*0.078+23.25+1.5 | PMOT*0.28+17.87+3.5 | PMOT*0.078+23.25+1.5 | PMOT*0.078+23.25-1.5 | PMOT*0.28+17.87-3.5 | PMOT*0.078+23.25-1.5 | YES | PMOT | 0.28+17.87 | 0.078+23.25 | 0.078+23.25 | 1.5 | 0.078+23.25 | 0.078+23.25 | -1.5 |  | 38.5 | 13 | 3.5 |  | 38.5 | 13 | -3.5
|  |  | 2 | ISO 7730 | All | 24 | PMOT*0.28+17.87+3.5 | 26 | 20 | PMOT*0.28+17.87-3.5 | 23 | YES | PMOT | 0.28+17.87 | 0.078+23.25 | 0.078+23.25 | 1.5 | 0.078+23.25 | 0.078+23.25 | -1.5 |  | 38.5 | 13 | 3.5 |  | 38.5 | 13 | -3.5
|  |  | 3 | Adap. Limits Horizont. Extended | All | 13*0.28+17.87+3.5 | PMOT*0.28+17.87+3.5 | 38.5*0.28+17.87+3.5 | 13*0.28+17.87-3.5 | PMOT*0.28+17.87-3.5 | 38.5*0.28+17.87-3.5 | YES | PMOT | 0.28+17.87 | 0.078+23.25 | 0.078+23.25 | 1.5 | 0.078+23.25 | 0.078+23.25 | -1.5 |  | 38.5 | 13 | 3.5 |  | 38.5 | 13 | -3.5
9 | IND IMAC R 7DRM | 80 | 0 |  | All | PMOT*0.078+23.25+2.72 | PMOT*0.078+23.25+3.6 | PMOT*0.078+23.25+3.6 | PMOT*0.078+23.25-2.72 | PMOT*0.078+23.25-3.6 | PMOT*0.078+23.25-3.6 | YES | PMOT | 0.078+23.25 | 0.078+23.25 | 0.078+23.25 | 2.72 | 0.078+23.25 | 0.078+23.25 | -2.72 |  | 33 | 5.5 | 3.6 |  | 33 | 5.5 | -3.6
|  |  | 1 | Indian Building Code | All | PMOT*0.078+23.25+2.72 | PMOT*0.39+18.42+3.6 | PMOT*0.078+23.25+2.72 | PMOT*0.078+23.25-2.72 | PMOT*0.39+18.42-3.6 | PMOT*0.078+23.25-2.72 | YES | PMOT | 0.39+18.42 | 0.078+23.25 | 0.078+23.25 | 2.72 | 0.078+23.25 | 0.078+23.25 | -2.72 |  | 33 | 5.5 | 3.6 |  | 33 | 5.5 | -3.6
|  |  | 2 | ISO 7730 | All | 25 | PMOT*0.39+18.42+3.6 | 27 | 19 | PMOT*0.39+18.42-3.6 | 22 | YES | PMOT | 0.39+18.42 | 0.078+23.25 | 0.078+23.25 | 2.72 | 0.078+23.25 | 0.078+23.25 | -2.72 |  | 33 | 5.5 | 3.6 |  | 33 | 5.5 | -3.6
|  |  | 3 | Adap. Limits Horizont. Extended | All | 5.5*0.39+18.42+3.6 | PMOT*0.39+18.42+3.6 | 33*0.39+18.42+3.6 | 5.5*0.39+18.42-3.6 | PMOT*0.39+18.42-3.6 | 33*0.39+18.42-3.6 | YES | PMOT | 0.39+18.42 | 0.078+23.25 | 0.078+23.25 | 2.72 | 0.078+23.25 | 0.078+23.25 | -2.72 |  | 33 | 5.5 | 3.6 |  | 33 | 5.5 | -3.6
|  | 90 | 0 |  | All | PMOT*0.078+23.25+1.5 | PMOT*0.078+23.25+2.15 | PMOT*0.078+23.25+2.15 | PMOT*0.078+23.25-1.5 | PMOT*0.078+23.25-2.15 | PMOT*0.078+23.25-2.15 | YES | PMOT | 0.078+23.25 | 0.078+23.25 | 0.078+23.25 | 1.5 | 0.078+23.25 | 0.078+23.25 | -1.5 |  | 33 | 5.5 | 2.15 |  | 33 | 5.5 | -2.15
|  |  | 1 | Indian Building Code | All | PMOT*0.078+23.25+1.5 | PMOT*0.39+18.42+2.15 | PMOT*0.078+23.25+1.5 | PMOT*0.078+23.25-1.5 | PMOT*0.39+18.42-2.15 | PMOT*0.078+23.25-1.5 | YES | PMOT | 0.39+18.42 | 0.078+23.25 | 0.078+23.25 | 1.5 | 0.078+23.25 | 0.078+23.25 | -1.5 |  | 33 | 5.5 | 2.15 |  | 33 | 5.5 | -2.15
|  |  | 2 | ISO 7730 | All | 24 | PMOT*0.39+18.42+2.15 | 26 | 20 | PMOT*0.39+18.42-2.15 | 23 | YES | PMOT | 0.39+18.42 | 0.078+23.25 | 0.078+23.25 | 1.5 | 0.078+23.25 | 0.078+23.25 | -1.5 |  | 33 | 5.5 | 2.15 |  | 33 | 5.5 | -2.15
|  |  | 3 | Adap. Limits Horizont. Extended | All | 5.5*0.39+18.42+2.15 | PMOT*0.39+18.42+2.15 | 33*0.39+18.42+2.15 | 5.5*0.39+18.42-2.15 | PMOT*0.39+18.42-2.15 | 33*0.39+18.42-2.15 | YES | PMOT | 0.39+18.42 | 0.078+23.25 | 0.078+23.25 | 1.5 | 0.078+23.25 | 0.078+23.25 | -1.5 |  | 33 | 5.5 | 2.15 |  | 33 | 5.5 | -2.15
10 | IND IMAC R 30DRM | 80 | 0 |  | All | RMOT*0.078+23.25+2.72 | RMOT*0.078+23.25+3.6 | RMOT*0.078+23.25+3.6 | RMOT*0.078+23.25-2.72 | RMOT*0.078+23.25-3.6 | RMOT*0.078+23.25-3.6 | YES | RMOT | 0.078+23.25 | 0.078+23.25 | 0.078+23.25 | 2.72 | 0.078+23.25 | 0.078+23.25 | -2.72 |  | 33 | 5.5 | 3.6 |  | 33 | 5.5 | -3.6
|  |  | 1 | Indian Building Code | All | RMOT*0.078+23.25+2.72 | RMOT*0.42+17.6+3.6 | RMOT*0.078+23.25+2.72 | RMOT*0.078+23.25-2.72 | RMOT*0.42+17.6-3.6 | RMOT*0.078+23.25-2.72 | YES | RMOT | 0.42+17.6 | 0.078+23.25 | 0.078+23.25 | 2.72 | 0.078+23.25 | 0.078+23.25 | -2.72 |  | 33 | 5.5 | 3.6 |  | 33 | 5.5 | -3.6
|  |  | 2 | ISO 7730 | All | 25 | RMOT*0.42+17.6+3.6 | 27 | 19 | RMOT*0.42+17.6-3.6 | 22 | YES | RMOT | 0.42+17.6 | 0.078+23.25 | 0.078+23.25 | 2.72 | 0.078+23.25 | 0.078+23.25 | -2.72 |  | 33 | 5.5 | 3.6 |  | 33 | 5.5 | -3.6
|  |  | 3 | Adap. Limits Horizont. Extended | All | 5.5*0.42+17.6+3.6 | RMOT*0.42+17.6+3.6 | 33*0.42+17.6+3.6 | 5.5*0.42+17.6-3.6 | RMOT*0.42+17.6-3.6 | 33*0.42+17.6-3.6 | YES | RMOT | 0.42+17.6 | 0.078+23.25 | 0.078+23.25 | 2.72 | 0.078+23.25 | 0.078+23.25 | -2.72 |  | 33 | 5.5 | 3.6 |  | 33 | 5.5 | -3.6
|  | 90 | 0 |  | All | RMOT*0.078+23.25+1.5 | RMOT*0.078+23.25+2.15 | RMOT*0.078+23.25+2.15 | RMOT*0.078+23.25-1.5 | RMOT*0.078+23.25-2.15 | RMOT*0.078+23.25-2.15 | YES | RMOT | 0.078+23.25 | 0.078+23.25 | 0.078+23.25 | 1.5 | 0.078+23.25 | 0.078+23.25 | -1.5 |  | 33 | 5.5 | 2.15 |  | 33 | 5.5 | -2.15
|  |  | 1 | Indian Building Code | All | RMOT*0.078+23.25+1.5 | RMOT*0.42+17.6+2.15 | RMOT*0.078+23.25+1.5 | RMOT*0.078+23.25-1.5 | RMOT*0.42+17.6-2.15 | RMOT*0.078+23.25-1.5 | YES | RMOT | 0.42+17.6 | 0.078+23.25 | 0.078+23.25 | 1.5 | 0.078+23.25 | 0.078+23.25 | -1.5 |  | 33 | 5.5 | 2.15 |  | 33 | 5.5 | -2.15
|  |  | 2 | ISO 7730 | All | 24 | RMOT*0.42+17.6+2.15 | 26 | 20 | RMOT*0.42+17.6-2.15 | 23 | YES | RMOT | 0.42+17.6 | 0.078+23.25 | 0.078+23.25 | 1.5 | 0.078+23.25 | 0.078+23.25 | -1.5 |  | 33 | 5.5 | 2.15 |  | 33 | 5.5 | -2.15
|  |  | 3 | Adap. Limits Horizont. Extended | All | 5.5*0.42+17.6+2.15 | RMOT*0.42+17.6+2.15 | 33*0.42+17.6+2.15 | 5.5*0.42+17.6-2.15 | RMOT*0.42+17.6-2.15 | 33*0.42+17.6-2.15 | YES | RMOT | 0.42+17.6 | 0.078+23.25 | 0.078+23.25 | 1.5 | 0.078+23.25 | 0.078+23.25 | -1.5 |  | 33 | 5.5 | 2.15 |  | 33 | 5.5 | -2.15
11 | IND Dhaka | 80 | 0 |  | All | RMOT*0.078+23.25+2.72 | RMOT*0.078+23.25+3.5 | RMOT*0.078+23.25+3.5 | RMOT*0.078+23.25-2.72 | RMOT*0.078+23.25-3.5 | RMOT*0.078+23.25-3.5 | YES | RMOT | 0.078+23.25 | 0.078+23.25 | 0.078+23.25 | 2.72 | 0.078+23.25 | 0.078+23.25 | -2.72 |  | ? | ? | 3.5 |  | ? | ? | -3.5
|  |  | 1 | Indian Building Code | All | RMOT*0.078+23.25+2.72 | RMOT*0.75+5.37+3.5 | RMOT*0.078+23.25+2.72 | RMOT*0.078+23.25-2.72 | RMOT*0.75+5.37-3.5 | RMOT*0.078+23.25-2.72 | YES | RMOT | 0.75+5.37 | 0.078+23.25 | 0.078+23.25 | 2.72 | 0.078+23.25 | 0.078+23.25 | -2.72 |  | ? | ? | 3.5 |  | ? | ? | -3.5
|  |  | 2 | ISO 7730 | All | 25 | RMOT*0.75+5.37+3.5 | 27 | 19 | RMOT*0.75+5.37-3.5 | 22 | YES | RMOT | 0.75+5.37 | 0.078+23.25 | 0.078+23.25 | 2.72 | 0.078+23.25 | 0.078+23.25 | -2.72 |  | ? | ? | 3.5 |  | ? | ? | -3.5
|  |  | 3 | Adap. Limits Horizont. Extended | All | ?*0.75+5.37+3.5 | RMOT*0.75+5.37+3.5 | ?*0.75+5.37+3.5 | ?*0.75+5.37-3.5 | RMOT*0.75+5.37-3.5 | ?*0.75+5.37-3.5 | YES | RMOT | 0.75+5.37 | 0.078+23.25 | 0.078+23.25 | 2.72 | 0.078+23.25 | 0.078+23.25 | -2.72 |  | ? | ? | 3.5 |  | ? | ? | -3.5
|  | 90 | 0 |  | All | RMOT*0.078+23.25+1.5 | RMOT*0.078+23.25+2.5 | RMOT*0.078+23.25+2.5 | RMOT*0.078+23.25-1.5 | RMOT*0.078+23.25-2.5 | RMOT*0.078+23.25-2.5 | YES | RMOT | 0.078+23.25 | 0.078+23.25 | 0.078+23.25 | 1.5 | 0.078+23.25 | 0.078+23.25 | -1.5 |  | ? | ? | 2.5 |  | ? | ? | -2.5
|  |  | 1 | Indian Building Code | All | RMOT*0.078+23.25+1.5 | RMOT*0.75+5.37+2.5 | RMOT*0.078+23.25+1.5 | RMOT*0.078+23.25-1.5 | RMOT*0.75+5.37-2.5 | RMOT*0.078+23.25-1.5 | YES | RMOT | 0.75+5.37 | 0.078+23.25 | 0.078+23.25 | 1.5 | 0.078+23.25 | 0.078+23.25 | -1.5 |  | ? | ? | 2.5 |  | ? | ? | -2.5
|  |  | 2 | ISO 7730 | All | 24 | RMOT*0.75+5.37+2.5 | 26 | 20 | RMOT*0.75+5.37-2.5 | 23 | YES | RMOT | 0.75+5.37 | 0.078+23.25 | 0.078+23.25 | 1.5 | 0.078+23.25 | 0.078+23.25 | -1.5 |  | ? | ? | 2.5 |  | ? | ? | -2.5
|  |  | 3 | Adap. Limits Horizont. Extended | All | ?*0.75+5.37+2.5 | RMOT*0.75+5.37+2.5 | ?*0.75+5.37+2.5 | ?*0.75+5.37-2.5 | RMOT*0.75+5.37-2.5 | ?*0.75+5.37-2.5 | YES | RMOT | 0.75+5.37 | 0.078+23.25 | 0.078+23.25 | 1.5 | 0.078+23.25 | 0.078+23.25 | -1.5 |  | ? | ? | 2.5 |  | ? | ? | -2.5
12 | ROM Udrea | 80 | 0 |  | All | 27 |  |  | 20 |  |  | YES | PMOT | 0.25+19.7 | [7 empty] | 33.5 | 10 | 2.89 |  | 33.5 | 10 | -2.89
|  |  | 1 | Romanian Building Code | All | 27 | PMOT*0.25+19.7+2.89 | 27 | 20 | PMOT*0.25+19.7-2.89 | 20 | YES | PMOT | 0.25+19.7 | [7 empty] | 33.5 | 10 | 2.89 |  | 33.5 | 10 | -2.89
|  |  | 2 | ISO 7730 | All | 25 | PMOT*0.25+19.7+2.89 | 27 | 19 | PMOT*0.25+19.7-2.89 | 22 | YES | PMOT | 0.25+19.7 | [7 empty] | 33.5 | 10 | 2.89 |  | 33.5 | 10 | -2.89
|  |  | 3 | Adap. Limits Horizont. Extended | All | 10*0.25+19.7+2.89 | PMOT*0.25+19.7+2.89 | 33.5*0.25+19.7+2.89 | 10*0.25+19.7-2.89 | PMOT*0.25+19.7-2.89 | 33.5*0.25+19.7-2.89 | YES | PMOT | 0.25+19.7 | [7 empty] | 33.5 | 10 | 2.89 |  | 33.5 | 10 | -2.89
|  | 90 | 0 |  | All | 25.5 |  |  | 21.5 |  |  | YES | PMOT | 0.25+19.7 | [7 empty] | 33.5 | 10 | 1.7 |  | 33.5 | 10 | -1.7
|  |  | 1 | Romanian Building Code | All | 25.5 | PMOT*0.25+19.7+1.7 | 25.5 | 21.5 | PMOT*0.25+19.7-1.7 | 21.5 | YES | PMOT | 0.25+19.7 | [7 empty] | 33.5 | 10 | 1.7 |  | 33.5 | 10 | -1.7
|  |  | 2 | ISO 7730 | All | 24 | PMOT*0.25+19.7+1.7 | 26 | 20 | PMOT*0.25+19.7-1.7 | 23 | YES | PMOT | 0.25+19.7 | [7 empty] | 33.5 | 10 | 1.7 |  | 33.5 | 10 | -1.7
|  |  | 3 | Adap. Limits Horizont. Extended | All | 10*0.25+19.7+1.7 | PMOT*0.25+19.7+1.7 | 33.5*0.25+19.7+1.7 | 10*0.25+19.7-1.7 | PMOT*0.25+19.7-1.7 | 33.5*0.25+19.7-1.7 | YES | PMOT | 0.25+19.7 | [7 empty] | 33.5 | 10 | 1.7 |  | 33.5 | 10 | -1.7
13 | AUS Williamson | 80 | 0.1 |  | CZ1, 2, 3 | 6:00 to 23:00: 27; else: 24 |  |  | 6:00 to 12:00: 20; else: 18 |  |  | YES
|  |  | 0.2 |  | CZ4 | 6:00 to 23:00: 26; else: 24 |  |  | 6:00 to 12:00: 20; else: 18 |  |  | YES
|  |  | 0.3 |  | CZ5 | 6:00 to 23:00: 25; else: 24 |  |  | 6:00 to 12:00: 20; else: 18 |  |  | YES
|  |  | 0.4 |  | CZ6, 7 | 6:00 to 23:00: 24; else: 24 |  |  | 6:00 to 12:00: 20; else: 18 |  |  | YES
|  |  | 0.5 |  | CZ8 | 6:00 to 23:00: 23; else: 24 |  |  | 6:00 to 12:00: 20; else: 18 |  |  | YES
|  |  | 1.1 | Australian Building Code | CZ1, 2, 3 | 6 to 23h: 27; else: 24 | RMOT*0.26+15.9+4.55 | 6 to 23h: 27; else: 24 | 6 to 12am: 20; else: 18 | RMOT*0.26+15.9-4.55 | 6 to 12am: 20; else: 18 | YES | RMOT | 0.26+15.9 | [7 empty] | 25 | 10 | 4.55 |  | 25 | 10 | -4.55
|  |  | 1.2 | Australian Building Code | CZ4 | 6 to 23h: 26; else: 24 | RMOT*0.26+15.9+4.55 | 6 to 23h: 26; else: 24 | 6 to 12am: 20; else: 18 | RMOT*0.26+15.9-4.55 | 6 to 12am: 20; else: 18 | YES | RMOT | 0.26+15.9 | [7 empty] | 25 | 10 | 4.55 |  | 25 | 10 | -4.55
|  |  | 1.3 | Australian Building Code | CZ5 | 6 to 23h: 25; else: 24 | RMOT*0.26+15.9+4.55 | 6 to 23h: 25; else: 24 | 6 to 12am: 20; else: 18 | RMOT*0.26+15.9-4.55 | 6 to 12am: 20; else: 18 | YES | RMOT | 0.26+15.9 | [7 empty] | 25 | 10 | 4.55 |  | 25 | 10 | -4.55
|  |  | 1.4 | Australian Building Code | CZ6, 7 | 6 to 23h: 24; else: 24 | RMOT*0.26+15.9+4.55 | 6 to 23h: 24; else: 24 | 6 to 12am: 20; else: 18 | RMOT*0.26+15.9-4.55 | 6 to 12am: 20; else: 18 | YES | RMOT | 0.26+15.9 | [7 empty] | 25 | 10 | 4.55 |  | 25 | 10 | -4.55
|  |  | 1.5 | Australian Building Code | CZ8 | 6 to 23h: 23; else: 24 | RMOT*0.26+15.9+4.55 | 6 to 23h: 23; else: 24 | 6 to 12am: 20; else: 18 | RMOT*0.26+15.9-4.55 | 6 to 12am: 20; else: 18 | YES | RMOT | 0.26+15.9 | [7 empty] | 25 | 10 | 4.55 |  | 25 | 10 | -4.55
|  |  | 2 | ISO 7730 | All | 25 | RMOT*0.26+15.9+4.55 | 27 | 19 | RMOT*0.26+15.9-4.55 | 22 | YES | RMOT | 0.26+15.9 | [7 empty] | 25 | 10 | 4.55 |  | 25 | 10 | -4.55
|  |  | 3 | Adap. Limits Horizont. Extended | All | 10*0.26+15.9+4.55 | RMOT*0.26+15.9+4.55 | 25*0.26+15.9+4.55 | 10*0.26+15.9-4.55 | RMOT*0.26+15.9-4.55 | 25*0.26+15.9-4.55 | YES | RMOT | 0.26+15.9 | [7 empty] | 25 | 10 | 4.55 |  | 25 | 10 | -4.55
|  | 90 | 0.1 |  | CZ1, 2, 3 | 6:00 to 23:00: 26; else: 23 |  |  | 6:00 to 12:00: 21; else: 19 |  |  | YES
|  |  | 0.2 |  | CZ4 | 6:00 to 23:00: 25; else: 23 |  |  | 6:00 to 12:00: 21; else: 19 |  |  | YES
|  |  | 0.3 |  | CZ5 | 6:00 to 23:00: 24; else: 23 |  |  | 6:00 to 12:00: 21; else: 19 |  |  | YES
|  |  | 0.4 |  | CZ6, 7 | 6:00 to 23:00: 23; else: 23 |  |  | 6:00 to 12:00: 21; else: 19 |  |  | YES
|  |  | 0.5 |  | CZ8 | 6:00 to 23:00: 22; else: 23 |  |  | 6:00 to 12:00: 21; else: 19 |  |  | YES
|  |  | 1.1 | Australian Building Code | CZ1, 2, 3 | 6 to 23h: 26; else: 23 | RMOT*0.26+15.9+3.45 | 6 to 23h: 26; else: 23 | 6 to 12am: 21; else: 19 | RMOT*0.26+15.9-3.45 | 6 to 12am: 21; else: 19 | YES | RMOT | 0.26+15.9 | [7 empty] | 25 | 10 | 3.45 |  | 25 | 10 | -3.45
|  |  | 1.2 | Australian Building Code | CZ4 | 6 to 23h: 25; else: 23 | RMOT*0.26+15.9+3.45 | 6 to 23h: 25; else: 23 | 6 to 12am: 21; else: 19 | RMOT*0.26+15.9-3.45 | 6 to 12am: 21; else: 19 | YES | RMOT | 0.26+15.9 | [7 empty] | 25 | 10 | 3.45 |  | 25 | 10 | -3.45
|  |  | 1.3 | Australian Building Code | CZ5 | 6 to 23h: 24; else: 23 | RMOT*0.26+15.9+3.45 | 6 to 23h: 24; else: 23 | 6 to 12am: 21; else: 19 | RMOT*0.26+15.9-3.45 | 6 to 12am: 21; else: 19 | YES | RMOT | 0.26+15.9 | [7 empty] | 25 | 10 | 3.45 |  | 25 | 10 | -3.45
|  |  | 1.4 | Australian Building Code | CZ6, 7 | 6 to 23h: 23; else: 23 | RMOT*0.26+15.9+3.45 | 6 to 23h: 23; else: 23 | 6 to 12am: 21; else: 19 | RMOT*0.26+15.9-3.45 | 6 to 12am: 21; else: 19 | YES | RMOT | 0.26+15.9 | [7 empty] | 25 | 10 | 3.45 |  | 25 | 10 | -3.45
|  |  | 1.5 | Australian Building Code | CZ8 | 6 to 23h: 22; else: 23 | RMOT*0.26+15.9+3.45 | 6 to 23h: 22; else: 23 | 6 to 12am: 21; else: 19 | RMOT*0.26+15.9-3.45 | 6 to 12am: 21; else: 19 | YES | RMOT | 0.26+15.9 | [7 empty] | 25 | 10 | 3.45 |  | 25 | 10 | -3.45
|  |  | 2 | ISO 7730 | All | 24 | RMOT*0.26+15.9+3.45 | 26 | 20 | RMOT*0.26+15.9-3.45 | 23 | YES | RMOT | 0.26+15.9 | [7 empty] | 25 | 10 | 3.45 |  | 25 | 10 | -3.45
|  |  | 3 | Adap. Limits Horizont. Extended | All | 10*0.26+15.9+3.45 | RMOT*0.26+15.9+3.45 | 25*0.26+15.9+3.45 | 10*0.26+15.9-3.45 | RMOT*0.26+15.9-3.45 | 25*0.26+15.9-3.45 | YES | RMOT | 0.26+15.9 | [7 empty] | 25 | 10 | 3.45 |  | 25 | 10 | -3.45
14 | AUS DeDear | 80 | 0.1 |  | CZ1, 2, 3 | 6:00 to 23:00: 27; else: 24 |  |  | 6:00 to 12:00: 20; else: 18 |  |  | YES | PMOT | 0.26+16.75 | [7 empty] | 27 | 8 | 4.5 |  | 27 | 8 | -4.5
|  |  | 0.2 |  | CZ4 | 6:00 to 23:00: 26; else: 24 |  |  | 6:00 to 12:00: 20; else: 18 |  |  | YES
|  |  | 0.3 |  | CZ5 | 6:00 to 23:00: 25; else: 24 |  |  | 6:00 to 12:00: 20; else: 18 |  |  | YES
|  |  | 0.4 |  | CZ6, 7 | 6:00 to 23:00: 24; else: 24 |  |  | 6:00 to 12:00: 20; else: 18 |  |  | YES
|  |  | 0.5 |  | CZ8 | 6:00 to 23:00: 23; else: 24 |  |  | 6:00 to 12:00: 20; else: 18 |  |  | YES
|  |  | 1.1 | Australian Building Code | CZ1, 2, 3 | 6 to 23h: 27; else: 24 | PMOT*0.26+16.75+4.5 | 6 to 23h: 27; else: 24 | 6 to 12am: 20; else: 18 | PMOT*0.26+16.75-4.5 | 6 to 12am: 20; else: 18 | YES | PMOT | 0.26+16.75 | [7 empty] | 27 | 8 | 4.5 |  | 27 | 8 | -4.5
|  |  | 1.2 | Australian Building Code | CZ4 | 6 to 23h: 26; else: 24 | PMOT*0.26+16.75+4.5 | 6 to 23h: 26; else: 24 | 6 to 12am: 20; else: 18 | PMOT*0.26+16.75-4.5 | 6 to 12am: 20; else: 18 | YES | PMOT | 0.26+16.75 | [7 empty] | 27 | 8 | 4.5 |  | 27 | 8 | -4.5
|  |  | 1.3 | Australian Building Code | CZ5 | 6 to 23h: 25; else: 24 | PMOT*0.26+16.75+4.5 | 6 to 23h: 25; else: 24 | 6 to 12am: 20; else: 18 | PMOT*0.26+16.75-4.5 | 6 to 12am: 20; else: 18 | YES | PMOT | 0.26+16.75 | [7 empty] | 27 | 8 | 4.5 |  | 27 | 8 | -4.5
|  |  | 1.4 | Australian Building Code | CZ6, 7 | 6 to 23h: 24; else: 24 | PMOT*0.26+16.75+4.5 | 6 to 23h: 24; else: 24 | 6 to 12am: 20; else: 18 | PMOT*0.26+16.75-4.5 | 6 to 12am: 20; else: 18 | YES | PMOT | 0.26+16.75 | [7 empty] | 27 | 8 | 4.5 |  | 27 | 8 | -4.5
|  |  | 1.5 | Australian Building Code | CZ8 | 6 to 23h: 23; else: 24 | PMOT*0.26+16.75+4.5 | 6 to 23h: 23; else: 24 | 6 to 12am: 20; else: 18 | PMOT*0.26+16.75-4.5 | 6 to 12am: 20; else: 18 | YES | PMOT | 0.26+16.75 | [7 empty] | 27 | 8 | 4.5 |  | 27 | 8 | -4.5
|  |  | 2 | ISO 7730 | All | 25 | PMOT*0.26+16.75+4.5 | 27 | 19 | PMOT*0.26+16.75-4.5 | 22 | YES | PMOT | 0.26+16.75 | [7 empty] | 27 | 8 | 4.5 |  | 27 | 8 | -4.5
|  |  | 3 | Adap. Limits Horizont. Extended | All | 8*0.26+16.75+4.5 | PMOT*0.26+16.75+4.5 | 27*0.26+16.75+4.5 | 8*0.26+16.75-4.5 | PMOT*0.26+16.75-4.5 | 27*0.26+16.75-4.5 | YES | PMOT | 0.26+16.75 | [7 empty] | 27 | 8 | 4.5 |  | 27 | 8 | -4.5
|  | 90 | 0.1 |  | CZ1, 2, 3 | 6:00 to 23:00: 26; else: 23 |  |  | 6:00 to 12:00: 21; else: 19 |  |  | YES
|  |  | 0.2 |  | CZ4 | 6:00 to 23:00: 25; else: 23 |  |  | 6:00 to 12:00: 21; else: 19 |  |  | YES
|  |  | 0.3 |  | CZ5 | 6:00 to 23:00: 24; else: 23 |  |  | 6:00 to 12:00: 21; else: 19 |  |  | YES
|  |  | 0.4 |  | CZ6, 7 | 6:00 to 23:00: 23; else: 23 |  |  | 6:00 to 12:00: 21; else: 19 |  |  | YES
|  |  | 0.5 |  | CZ8 | 6:00 to 23:00: 22; else: 23 |  |  | 6:00 to 12:00: 21; else: 19 |  |  | YES
|  |  | 1.1 | Australian Building Code | CZ1, 2, 3 | 6 to 23h: 26; else: 23 | PMOT*0.26+16.75+3.5 | 6 to 23h: 26; else: 23 | 6 to 12am: 21; else: 19 | PMOT*0.26+16.75-3.5 | 6 to 12am: 21; else: 19 | YES | PMOT | 0.26+16.75 | [7 empty] | 27 | 8 | 3.5 |  | 27 | 8 | -3.5
|  |  | 1.2 | Australian Building Code | CZ4 | 6 to 23h: 25; else: 23 | PMOT*0.26+16.75+3.5 | 6 to 23h: 25; else: 23 | 6 to 12am: 21; else: 19 | PMOT*0.26+16.75-3.5 | 6 to 12am: 21; else: 19 | YES | PMOT | 0.26+16.75 | [7 empty] | 27 | 8 | 3.5 |  | 27 | 8 | -3.5
|  |  | 1.3 | Australian Building Code | CZ5 | 6 to 23h: 24; else: 23 | PMOT*0.26+16.75+3.5 | 6 to 23h: 24; else: 23 | 6 to 12am: 21; else: 19 | PMOT*0.26+16.75-3.5 | 6 to 12am: 21; else: 19 | YES | PMOT | 0.26+16.75 | [7 empty] | 27 | 8 | 3.5 |  | 27 | 8 | -3.5
|  |  | 1.4 | Australian Building Code | CZ6, 7 | 6 to 23h: 23; else: 23 | PMOT*0.26+16.75+3.5 | 6 to 23h: 23; else: 23 | 6 to 12am: 21; else: 19 | PMOT*0.26+16.75-3.5 | 6 to 12am: 21; else: 19 | YES | PMOT | 0.26+16.75 | [7 empty] | 27 | 8 | 3.5 |  | 27 | 8 | -3.5
|  |  | 1.5 | Australian Building Code | CZ8 | 6 to 23h: 22; else: 23 | PMOT*0.26+16.75+3.5 | 6 to 23h: 22; else: 23 | 6 to 12am: 21; else: 19 | PMOT*0.26+16.75-3.5 | 6 to 12am: 21; else: 19 | YES | PMOT | 0.26+16.75 | [7 empty] | 27 | 8 | 3.5 |  | 27 | 8 | -3.5
|  |  | 2 | ISO 7730 | All | 24 | PMOT*0.26+16.75+3.5 | 26 | 20 | PMOT*0.26+16.75-3.5 | 23 | YES | PMOT | 0.26+16.75 | [7 empty] | 27 | 8 | 3.5 |  | 27 | 8 | -3.5
|  |  | 3 | Adap. Limits Horizont. Extended | All | 8*0.26+16.75+3.5 | PMOT*0.26+16.75+3.5 | 27*0.26+16.75+3.5 | 8*0.26+16.75-3.5 | PMOT*0.26+16.75-3.5 | 27*0.26+16.75-3.5 | YES | PMOT | 0.26+16.75 | [7 empty] | 27 | 8 | 3.5 |  | 27 | 8 | -3.5
15 | BRA Rupp NV | 80 | 0 |  | WS | 23.5 |  |  | 21 |  |  | YES |  | 0.56+12.74 | [7 empty] | 24.8 | 16.9 | 3.8 |  | 24.8 | 16.9 | -3.8
[5 empty] | SS | 25.5 |  |  | 22.5 |  |  | YES
|  |  | 1 | ABNT NBR 16401-2 Standard | All | 23.5 | PMOT*0.56+12.74+3.8 | 25.5 | 21 | PMOT*0.56+12.74-3.8 | 22.5 | YES | PMOT | 0.56+12.74 | [7 empty] | 24.8 | 16.9 | 3.8 |  | 24.8 | 16.9 | -3.8
|  |  | 2 | ISO 7730 | All | 25 | PMOT*0.56+12.74+3.8 | 27 | 19 | PMOT*0.56+12.74-3.8 | 22 | YES | PMOT | 0.56+12.74 | [7 empty] | 24.8 | 16.9 | 3.8 |  | 24.8 | 16.9 | -3.8
|  |  | 3 | Adap. Limits Horizont. Extended | All | 16.9*0.56+12.74+3.8 | PMOT*0.56+12.74+3.8 | 24.8*0.56+12.74+3.8 | 16.9*0.56+12.74-3.8 | PMOT*0.56+12.74-3.8 | 24.8*0.56+12.74-3.8 | YES | PMOT | 0.56+12.74 | [7 empty] | 24.8 | 16.9 | 3.8 |  | 24.8 | 16.9 | -3.8
|  | 90 | 0 |  | WS | 23 |  |  | 21.5 |  |  | YES
[5 empty] | SS | 25 |  |  | 23 |  |  | YES | PMOT | 0.56+12.74 | [7 empty] | 24.8 | 16.9 | 2.8 |  | 24.8 | 16.9 | -2.8
|  |  | 1 | ABNT NBR 16401-2 Standard | All | 23 | PMOT*0.56+12.74+2.8 | 25 | 21.5 | PMOT*0.56+12.74-2.8 | 23 | YES | PMOT | 0.56+12.74 | [7 empty] | 24.8 | 16.9 | 2.8 |  | 24.8 | 16.9 | -2.8
|  |  | 2 | ISO 7730 | All | 24 | PMOT*0.56+12.74+2.8 | 26 | 20 | PMOT*0.56+12.74-2.8 | 23 | YES | PMOT | 0.56+12.74 | [7 empty] | 24.8 | 16.9 | 2.8 |  | 24.8 | 16.9 | -2.8
|  |  | 3 | Adap. Limits Horizont. Extended | All | 16.9*0.56+12.74+2.8 | PMOT*0.56+12.74+2.8 | 24.8*0.56+12.74+2.8 | 16.9*0.56+12.74-2.8 | PMOT*0.56+12.74-2.8 | 24.8*0.56+12.74-2.8 | YES | PMOT | 0.56+12.74 | [7 empty] | 24.8 | 16.9 | 2.8 |  | 24.8 | 16.9 | -2.8
16 | BRA Rupp AC | 80 | 0 |  | WS | 23.5 |  |  | 21 |  |  | YES | PMOT | 0.09+22.32 | [7 empty] | 25.7 | 16.4 | 2.1 |  | 25.7 | 16.4 | -2.1
[5 empty] | SS | 25.5 |  |  | 22.5
|  |  | 1 | ABNT NBR 16401-2 Standard | All | 23.5 | PMOT*0.09+22.32+2.1 | 25.5 | 21 | PMOT*0.09+22.32-2.1 | 22.5 | YES | PMOT | 0.09+22.32 | [7 empty] | 25.7 | 16.4 | 2.1 |  | 25.7 | 16.4 | -2.1
|  |  | 2 | ISO 7730 | All | 25 | PMOT*0.09+22.32+2.1 | 27 | 19 | PMOT*0.09+22.32-2.1 | 22 | YES | PMOT | 0.09+22.32 | [7 empty] | 25.7 | 16.4 | 2.1 |  | 25.7 | 16.4 | -2.1
|  |  | 3 | Limits Horizont. Extended | All | 16.4*0.09+22.32+2.1 | PMOT*0.09+22.32+2.1 | 25.7*0.09+22.32+2.1 | 16.4*0.09+22.32-2.1 | PMOT*0.09+22.32-2.1 | 25.7*0.09+22.32-2.1 | YES | PMOT | 0.09+22.32 | [7 empty] | 25.7 | 16.4 | 2.1 |  | 25.7 | 16.4 | -2.1
|  | 90 | 0 |  | WS | 23 |  |  | 21.5 |  |  | YES | PMOT | 0.09+22.32 | [7 empty] | 25.7 | 16.4 | 1.1 |  | 25.7 | 16.4 | -1.1
[5 empty] | SS | 25 |  |  | 23
|  |  | 1 | ABNT NBR 16401-2 Standard | All | 25 | PMOT*0.09+22.32+1.1 | 25 | 23 | PMOT*0.09+22.32-1.1 | 23 | YES | PMOT | 0.09+22.32 | [7 empty] | 25.7 | 16.4 | 1.1 |  | 25.7 | 16.4 | -1.1
|  |  | 2 | ISO 7730 | All | 24 | PMOT*0.09+22.32+1.1 | 26 | 20 | PMOT*0.09+22.32-1.1 | 23 | YES | PMOT | 0.09+22.32 | [7 empty] | 25.7 | 16.4 | 1.1 |  | 25.7 | 16.4 | -1.1
|  |  | 3 | Limits Horizont. Extended | All | 16.4*0.09+22.32+1.1 | PMOT*0.09+22.32+1.1 | 25.7*0.09+22.32+1.1 | 16.4*0.09+22.32-1.1 | PMOT*0.09+22.32-1.1 | 25.7*0.09+22.32-1.1 | YES | PMOT | 0.09+22.32 | [7 empty] | 25.7 | 16.4 | 1.1 |  | 25.7 | 16.4 | -1.1
17 | MEX Oropeza Arid | 80 | 0 |  | All | 25 |  |  | 20 |  |  |  | PMOT
|  |  | 1 | Relevant static setpoints for Mex | WS | 25 | PMOT*0.48+13.9+3 | 25 | 20 | PMOT*0.48+13.9-3 | 20 |  | PMOT | 0.48+13.9 | [7 empty] | 25.25 | 11.25 | 3 |  | 25.25 | 11.25 | -3
[5 empty] | SS | 25 | PMOT*0.59+9.6+3 | 25 | 20 | PMOT*0.59+9.6-3 | 20 |  | PMOT | 0.59+9.6 | [7 empty] | 45 | 23 | 3 |  | 45 | 23 | -3
|  |  | 2 | ISO 7730 | WS | 27 | PMOT*0.48+13.9+3 | 25 | 19 | PMOT*0.48+13.9-3 | 22 |  | PMOT | 0.48+13.9 | [7 empty] | 25.25 | 11.25 | 3 |  | 25.25 | 11.25 | -3
[5 empty] | SS | 27 | PMOT*0.59+9.6+3 | 25 | 19 | PMOT*0.59+9.6-3 | 22 |  | PMOT | 0.59+9.6 | [7 empty] | 45 | 23 | 3 |  | 45 | 23 | -3
|  |  | 3 | Adap. Limits Horizont. Extended | WS | 11.25*0.48+13.9+3 | PMOT*0.48+13.9+3 | 25.25*0.48+13.9+3 | 11.25*0.48+13.9-3 | PMOT*0.48+13.9-3 | 25.25*0.48+13.9-3 |  | PMOT | 0.48+13.9 | [7 empty] | 25.25 | 11.25 | 3 |  | 25.25 | 11.25 | -3
[5 empty] | SS | 23*0.59+9.6+3 | PMOT*0.59+9.6+3 | 45*0.59+9.6+3 | 23*0.59+9.6-3 | PMOT*0.59+9.6-3 | 45*0.59+9.6-3 |  | PMOT | 0.59+9.6 | [7 empty] | 45 | 23 | 3 |  | 45 | 23 | -3
|  | 90 | 0 |  | All | 25 |  |  | 20 |  |  |  | PMOT
|  |  | 1 | Relevant static setpoints for Mex | WS | 25 | PMOT*0.48+13.9+2 | 25 | 20 | PMOT*0.48+13.9-2 | 20 |  | PMOT | 0.48+13.9 | [7 empty] | 25.25 | 11.25 | 2 |  | 25.25 | 11.25 | -2
[5 empty] | SS | 25 | PMOT*0.59+9.6+2 | 25 | 20 | PMOT*0.59+9.6-2 | 20 |  | PMOT | 0.59+9.6 | [7 empty] | 45 | 23 | 2 |  | 45 | 23 | -2
|  |  | 2 | ISO 7730 | WS | 26 | PMOT*0.48+13.9+2 | 24 | 20 | PMOT*0.48+13.9-2 | 23 |  | PMOT | 0.48+13.9 | [7 empty] | 25.25 | 11.25 | 2 |  | 25.25 | 11.25 | -2
[5 empty] | SS | 26 | PMOT*0.59+9.6+2 | 24 | 20 | PMOT*0.59+9.6-2 | 23 |  | PMOT | 0.59+9.6 | [7 empty] | 45 | 23 | 2 |  | 45 | 23 | -2
|  |  | 3 | Adap. Limits Horizont. Extended | WS | 11.25*0.48+13.9+2 | PMOT*0.48+13.9+2 | 25.25*0.48+13.9+2 | 11.25*0.48+13.9-2 | PMOT*0.48+13.9-2 | 25.25*0.48+13.9-2 |  | PMOT | 0.48+13.9 | [7 empty] | 25.25 | 11.25 | 2 |  | 25.25 | 11.25 | -2
[5 empty] | SS | 23*0.59+9.6+2 | PMOT*0.59+9.6+2 | 45*0.59+9.6+2 | 23*0.59+9.6-2 | PMOT*0.59+9.6-2 | 45*0.59+9.6-2 |  | PMOT | 0.59+9.6 | [7 empty] | 45 | 23 | 2 |  | 45 | 23 | -2
18 | MEX Oropeza DryTropic | 80 | 0 |  | All | 25 |  |  | 20 |  |  |  | PMOT
|  |  | 1 | Relevant static setpoints for Mex | WS | 25 | PMOT*0.84+5.3+3 | 25 | 20 | PMOT*0.84+5.3-3 | 20 |  | PMOT | 0.84+5.3 | [7 empty] | 27.5 | 15.5 | 3 |  | 27.5 | 15.5 | -3
[5 empty] | SS | 25 | PMOT*0.96-3.6+3 | 25 | 20 | PMOT*0.96-3.6-3 | 20 |  | PMOT | 0.96-3.6 | [7 empty] | 34 | 23 | 3 |  | 34 | 23 | -3
|  |  | 2 | ISO 7730 | WS | 27 | PMOT*0.84+5.3+3 | 25 | 19 | PMOT*0.84+5.3-3 | 22 |  | PMOT | 0.84+5.3 | [7 empty] | 27.5 | 15.5 | 3 |  | 27.5 | 15.5 | -3
[5 empty] | SS | 27 | PMOT*0.96-3.6+3 | 25 | 19 | PMOT*0.96-3.6-3 | 22 |  | PMOT | 0.96-3.6 | [7 empty] | 34 | 23 | 3 |  | 34 | 23 | -3
|  |  | 3 | Adap. Limits Horizont. Extended | WS | 15.5*0.84+5.3+3 | PMOT*0.84+5.3+3 | 27.5*0.84+5.3+3 | 15.5*0.84+5.3-3 | PMOT*0.84+5.3-3 | 27.5*0.84+5.3-3 |  | PMOT | 0.84+5.3 | [7 empty] | 27.5 | 15.5 | 3 |  | 27.5 | 15.5 | -3
[5 empty] | SS | 23*0.96-3.6+3 | PMOT*0.96-3.6+3 | 34*0.96-3.6+3 | 23*0.96-3.6-3 | PMOT*0.96-3.6-3 | 34*0.96-3.6-3 |  | PMOT | 0.96-3.6 | [7 empty] | 34 | 23 | 3 |  | 34 | 23 | -3
|  | 90 | 0 |  | All | 25 |  |  | 20 |  |  |  | PMOT
|  |  | 1 | Relevant static setpoints for Mex | WS | 25 | PMOT*0.84+5.3+2 | 25 | 20 | PMOT*0.84+5.3-2 | 20 |  | PMOT | 0.84+5.3 | [7 empty] | 27.5 | 15.5 | 2 |  | 27.5 | 15.5 | -2
[5 empty] | SS | 25 | PMOT*0.96-3.6+2 | 25 | 20 | PMOT*0.96-3.6-2 | 20 |  | PMOT | 0.96-3.6 | [7 empty] | 34 | 23 | 2 |  | 34 | 23 | -2
|  |  | 2 | ISO 7730 | WS | 26 | PMOT*0.84+5.3+2 | 24 | 20 | PMOT*0.84+5.3-2 | 23 |  | PMOT | 0.84+5.3 | [7 empty] | 27.5 | 15.5 | 2 |  | 27.5 | 15.5 | -2
[5 empty] | SS | 26 | PMOT*0.96-3.6+2 | 24 | 20 | PMOT*0.96-3.6-2 | 23 |  | PMOT | 0.96-3.6 | [7 empty] | 34 | 23 | 2 |  | 34 | 23 | -2
|  |  | 3 | Adap. Limits Horizont. Extended | WS | 15.5*0.84+5.3+2 | PMOT*0.84+5.3+2 | 27.5*0.84+5.3+2 | 15.5*0.84+5.3-2 | PMOT*0.84+5.3-2 | 27.5*0.84+5.3-2 |  | PMOT | 0.84+5.3 | [7 empty] | 27.5 | 15.5 | 2 |  | 27.5 | 15.5 | -2
[5 empty] | SS | 23*0.96-3.6+2 | PMOT*0.96-3.6+2 | 34*0.96-3.6+2 | 23*0.96-3.6-2 | PMOT*0.96-3.6-2 | 34*0.96-3.6-2 |  | PMOT | 0.96-3.6 | [7 empty] | 34 | 23 | 2 |  | 34 | 23 | -2
19 | MEX Oropeza Temperate | 80 | 0 |  | All | 25 |  |  | 20 |  |  |  | PMOT
|  |  | 1 | Relevant static setpoints for Mex | WS | 25 | PMOT*0.27+17.9+2 | 25 | 20 | PMOT*0.27+17.9-2 | 20 |  | PMOT | 0.27+17.9 | [7 empty] | 25.25 | 5 | 2 |  | 25.25 | 5 | -2
[5 empty] | SS | 25 | PMOT*0.53+10.3+1 | 25 | 20 | PMOT*0.53+10.3-1 | 20 |  | PMOT | 0.53+10.3 | [7 empty] | 25.25 | 11.75 | 1 |  | 25.25 | 11.75 | -1
|  |  | 2 | ISO 7730 | WS | 27 | PMOT*0.27+17.9+2 | 25 | 19 | PMOT*0.27+17.9-2 | 22 |  | PMOT | 0.27+17.9 | [7 empty] | 25.25 | 5 | 2 |  | 25.25 | 5 | -2
[5 empty] | SS | 27 | PMOT*0.53+10.3+1 | 25 | 19 | PMOT*0.53+10.3-1 | 22 |  | PMOT | 0.53+10.3 | [7 empty] | 25.25 | 11.75 | 1 |  | 25.25 | 11.75 | -1
|  |  | 3 | Adap. Limits Horizont. Extended | WS | 5*0.27+17.9+2 | PMOT*0.27+17.9+2 | 25.25*0.27+17.9+2 | 5*0.27+17.9-2 | PMOT*0.27+17.9-2 | 25.25*0.27+17.9-2 |  | PMOT | 0.27+17.9 | [7 empty] | 25.25 | 5 | 2 |  | 25.25 | 5 | -2
[5 empty] | SS | 11.75*0.53+10.3+1 | PMOT*0.53+10.3+1 | 25.25*0.53+10.3+1 | 11.75*0.53+10.3-1 | PMOT*0.53+10.3-1 | 25.25*0.53+10.3-1 |  | PMOT | 0.53+10.3 | [7 empty] | 25.25 | 11.75 | 1 |  | 25.25 | 11.75 | -1
|  | 90 | 0 |  | All | 25 |  |  | 20 |  |  |  | PMOT
|  |  | 1 | Relevant static setpoints for Mex | WS | 25 | PMOT*0.27+17.9+3 | 25 | 20 | PMOT*0.27+17.9-3 | 20 |  | PMOT | 0.27+17.9 | [7 empty] | 25.25 | 5 | 3 |  | 25.25 | 5 | -3
[5 empty] | SS | 25 | PMOT*0.53+10.3+2 | 25 | 20 | PMOT*0.53+10.3-2 | 20 |  | PMOT | 0.53+10.3 | [7 empty] | 25.25 | 11.75 | 2 |  | 25.25 | 11.75 | -2
|  |  | 2 | ISO 7730 | WS | 26 | PMOT*0.27+17.9+3 | 24 | 20 | PMOT*0.27+17.9-3 | 23 |  | PMOT | 0.27+17.9 | [7 empty] | 25.25 | 5 | 3 |  | 25.25 | 5 | -3
[5 empty] | SS | 26 | PMOT*0.53+10.3+2 | 24 | 20 | PMOT*0.53+10.3-2 | 23 |  | PMOT | 0.53+10.3 | [7 empty] | 25.25 | 11.75 | 2 |  | 25.25 | 11.75 | -2
|  |  | 3 | Adap. Limits Horizont. Extended | WS | 5*0.27+17.9+3 | PMOT*0.27+17.9+3 | 25.25*0.27+17.9+3 | 5*0.27+17.9-3 | PMOT*0.27+17.9-3 | 25.25*0.27+17.9-3 |  | PMOT | 0.27+17.9 | [7 empty] | 25.25 | 5 | 3 |  | 25.25 | 5 | -3
[5 empty] | SS | 11.75*0.53+10.3+2 | PMOT*0.53+10.3+2 | 25.25*0.53+10.3+2 | 11.75*0.53+10.3-2 | PMOT*0.53+10.3-2 | 25.25*0.53+10.3-2 |  | PMOT | 0.53+10.3 | [7 empty] | 25.25 | 11.75 | 2 |  | 25.25 | 11.75 | -2
20 | MEX Oropeza HumTropic | 80 | 0 |  | All | 25 |  |  | 20 |  |  |  | PMOT
|  |  | 1 | Relevant static setpoints for Mex | WS | 25 | PMOT*0.38+15.7+2 | 25 | 20 | PMOT*0.38+15.7-2 | 20 |  | PMOT | 0.38+15.7 | [7 empty] | 29.75 | 13 | 2 |  | 29.75 | 13 | -2
[5 empty] | SS | 25 | PMOT*0.47+9.07+5 | 25 | 20 | PMOT*0.47+9.07-5 | 20 |  | PMOT | 0.47+9.07 | [7 empty] | 45 | 23 | 5 |  | 45 | 23 | -5
|  |  | 2 | ISO 7730 | WS | 27 | PMOT*0.38+15.7+2 | 25 | 19 | PMOT*0.38+15.7-2 | 22 |  | PMOT | 0.38+15.7 | [7 empty] | 29.75 | 13 | 2 |  | 29.75 | 13 | -2
[5 empty] | SS | 27 | PMOT*0.47+9.07+5 | 25 | 19 | PMOT*0.47+9.07-5 | 22 |  | PMOT | 0.47+9.07 | [7 empty] | 45 | 23 | 5 |  | 45 | 23 | -5
|  |  | 3 | Adap. Limits Horizont. Extended | WS | 13*0.38+15.7+2 | PMOT*0.38+15.7+2 | 29.75*0.38+15.7+2 | 13*0.38+15.7-2 | PMOT*0.38+15.7-2 | 29.75*0.38+15.7-2 |  | PMOT | 0.38+15.7 | [7 empty] | 29.75 | 13 | 2 |  | 29.75 | 13 | -2
[5 empty] | SS | 23*0.47+9.07+5 | PMOT*0.47+9.07+5 | 45*0.47+9.07+5 | 23*0.47+9.07-5 | PMOT*0.47+9.07-5 | 45*0.47+9.07-5 |  | PMOT | 0.47+9.07 | [7 empty] | 45 | 23 | 5 |  | 45 | 23 | -5
|  | 90 | 0 |  | All | 25 |  |  | 20 |  |  |  | PMOT
|  |  | 1 | Relevant static setpoints for Mex | WS | 25 | PMOT*0.38+15.7+3 | 25 | 20 | PMOT*0.38+15.7-3 | 20 |  | PMOT | 0.38+15.7 | [7 empty] | 29.75 | 13 | 3 |  | 29.75 | 13 | -3
[5 empty] | SS | 25 | PMOT*0.47+9.07+6 | 25 | 20 | PMOT*0.47+9.07-6 | 20 |  | PMOT | 0.47+9.07 | [7 empty] | 45 | 23 | 6 |  | 45 | 23 | -6
|  |  | 2 | ISO 7730 | WS | 26 | PMOT*0.38+15.7+3 | 24 | 20 | PMOT*0.38+15.7-3 | 23 |  | PMOT | 0.38+15.7 | [7 empty] | 29.75 | 13 | 3 |  | 29.75 | 13 | -3
[5 empty] | SS | 26 | PMOT*0.47+9.07+6 | 24 | 20 | PMOT*0.47+9.07-6 | 23 |  | PMOT | 0.47+9.07 | [7 empty] | 45 | 23 | 6 |  | 45 | 23 | -6
|  |  | 3 | Adap. Limits Horizont. Extended | WS | 13*0.38+15.7+3 | PMOT*0.38+15.7+3 | 29.75*0.38+15.7+3 | 13*0.38+15.7-3 | PMOT*0.38+15.7-3 | 29.75*0.38+15.7-3 |  | PMOT | 0.38+15.7 | [7 empty] | 29.75 | 13 | 3 |  | 29.75 | 13 | -3
[5 empty] | SS | 23*0.47+9.07+6 | PMOT*0.47+9.07+6 | 45*0.47+9.07+6 | 23*0.47+9.07-6 | PMOT*0.47+9.07-6 | 45*0.47+9.07-6 |  | PMOT | 0.47+9.07 | [7 empty] | 45 | 23 | 6 |  | 45 | 23 | -6
21 | CHL Perez-Fargallo | 80 | 0 | ? | All | ? |  |  | ? |  |  | NO | PMOT | 0.678+13.51 | [7 empty] | 20 | 6.5 | 4 |  | 20 | 6.5 | -4
|  |  | 1 | ? | All | ? | ? | ? | ? | ? | ? | NO | PMOT | 0.678+13.51 | [7 empty] | 20 | 6.5 | 4 |  | 20 | 6.5 | -4
|  |  | 2 | ISO 7730 | All | 25 | PMOT*0.678+13.51+4 | 27 | 19 | PMOT*0.678+13.51-4 | 22 | YES | PMOT | 0.678+13.51 | [7 empty] | 20 | 6.5 | 4 |  | 20 | 6.5 | -4
|  |  | 3 | Adap. Limits Horizont. Extended | All | 6.5*0.678+13.51+4 | PMOT*0.678+13.51+4 | 20*0.678+13.51+4 | 6.5*0.678+13.51-4 | PMOT*0.678+13.51-4 | 20*0.678+13.51-4 | YES | PMOT | 0.678+13.51 | [7 empty] | 20 | 6.5 | 4 |  | 20 | 6.5 | -4
|  | 90 | 0 | ? | All | ? |  |  | ? |  |  | NO | PMOT | 0.678+13.51 | [7 empty] | 20 | 6.5 | 2.5 |  | 20 | 6.5 | -2.5
|  |  | 1 | ? | All | ? | ? | ? | ? | ? | ? | NO | PMOT | 0.678+13.51 | [7 empty] | 20 | 6.5 | 2.5 |  | 20 | 6.5 | -2.5
|  |  | 2 | ISO 7730 | All | 24 | PMOT*0.678+13.51+2.5 | 26 | 20 | PMOT*0.678+13.51-2.5 | 23 | YES | PMOT | 0.678+13.51 | [7 empty] | 20 | 6.5 | 2.5 |  | 20 | 6.5 | -2.5
|  |  | 3 | Adap. Limits Horizont. Extended | All | 6.5*0.678+13.51+2.5 | PMOT*0.678+13.51+2.5 | 20*0.678+13.51+2.5 | 6.5*0.678+13.51-2.5 | PMOT*0.678+13.51-2.5 | 20*0.678+13.51-2.5 | YES | PMOT | 0.678+13.51 | [7 empty] | 20 | 6.5 | 2.5 |  | 20 | 6.5 | -2.5
22 | INT ISO7730 | 1: A | 0 | - | WS | 23 |  |  | 21
|  |  |  | - | SS | 25.5 |  |  | 23.5
|  | 2: B | 0 | - | WS | 24 |  |  | 20
|  |  |  | - | SS | 26 |  |  | 23
|  | 3: C | 0 | - | WS | 25 |  |  | 19
|  |  |  | - | SS | 27 |  |  | 22
PMOT: Prevailing mean outdoor temperature; RMOT: Running mean outdoor temperature; WS: Winter season; SS: Summer season; NA: Not applicable;
ACSTall: Adaptive Cooling Setpoint Temperature applicability lower limit; ACSTaul: Adaptive Cooling Setpoint Temperature applicability upper limit;
AHSTall: Adaptive Heating Setpoint Temperature applicability lower limit; AHSTaul: Adaptive Heating Setpoint Temperature applicability upper limit;
WMOT: Weighted Mean Outdoor Temperature (can be either RMOT or PMOT)
?: Functions to be added

## References
ComfStand No. | ComfStand Name | Area | Reference
0 | ESP CTE | Spain | The Government of Spain. Royal Decree 314/2006. Approving the Spanish Technical Building Code CTE-DB-HE-1 2013:1–43. https://www.boe.es/eli/es/rd/2006/03/17/314 (accessed August 6, 2021).
1 | INT EN16798 | Europe | European committee for standardization. EN 16798-1:2019 Energy performance of buildings. Ventilation for buildings. Indoor environmental input parameters for design and assessment of energy performance of buildings addressing indoor air quality, thermal environment, lighting and acoustics. 2019. https://en.tienda.aenor.com/norma-bsi-bs-en-16798-1-2019-000000000030297474 (accessed August 6, 2021).
2 | INT ASHRAE55 | Worldwide | ASHRAE Standard 55-2020 Thermal Environmental Conditions for Human Occupancy, ASHRAE Standard (2020).
3 | JPN Rijal | Japan | Rijal, H. B., Humphreys, M. A., & Nicol, J. F. (2019). Adaptive model and the adaptive mechanisms for thermal comfort in Japanese dwellings. Energy and Buildings, 202, 109371. https://doi.org/10.1016/j.enbuild.2019.109371
4 | CHN GBT50785 Cold | China | MOHURD, Evaluation Standard for Indoor Thermal Environment in Civil Buildings (GB/T 50785-2012), Ministry of Housing and Urban-Rural Development (MOHURD), Beijing, China, 2012.
5 | CHN GBT50785 HotMild | China | MOHURD, Evaluation Standard for Indoor Thermal Environment in Civil Buildings (GB/T 50785-2012), Ministry of Housing and Urban-Rural Development (MOHURD), Beijing, China, 2012.
6 | CHN Yang | China | Yang, L., Fu, R., He, W., He, Q., & Liu, Y. (2020). Adaptive thermal comfort and climate responsive building design strategies in dry–hot and dry–cold areas: Case study in Turpan, China. Energy and Buildings, 209, 109678. https://doi.org/10.1016/j.enbuild.2019.109678
7 | IND IMAC C NV | India | Manu, S., Shukla, Y., Rawal, R., Thomas, L. E., & de Dear, R. (2016). Field studies of thermal comfort across multiple climate zones for the subcontinent: India Model for Adaptive Comfort (IMAC). Building and Environment, 98, 55–70. https://doi.org/10.1016/j.buildenv.2015.12.019
8 | IND IMAC C MM | India | Manu, S., Shukla, Y., Rawal, R., Thomas, L. E., & de Dear, R. (2016). Field studies of thermal comfort across multiple climate zones for the subcontinent: India Model for Adaptive Comfort (IMAC). Building and Environment, 98, 55–70. https://doi.org/10.1016/j.buildenv.2015.12.019
9 | IND IMAC R 7DRM | India | Rawal, R., Shukla, Y., Vardhan, V., Asrani, S., Schweiker, M., de Dear, R., Garg, V., Mathur, J., Prakash, S., Diddi, S., Ranjan, S. V., Siddiqui, A. N., & Somani, G. (2022). Adaptive thermal comfort model based on field studies in five climate zones across India. Building and Environment, 219, 109187. https://doi.org/10.1016/J.BUILDENV.2022.109187
10 | IND IMAC R 30DRM | India | Rawal, R., Shukla, Y., Vardhan, V., Asrani, S., Schweiker, M., de Dear, R., Garg, V., Mathur, J., Prakash, S., Diddi, S., Ranjan, S. V., Siddiqui, A. N., & Somani, G. (2022). Adaptive thermal comfort model based on field studies in five climate zones across India. Building and Environment, 219, 109187. https://doi.org/10.1016/J.BUILDENV.2022.109187
11 | IND Dhaka | India | Dhaka, S., Mathur, J., Brager, G., & Honnekeri, A. (2015). Assessment of thermal environmental conditions and quantification of thermal adaptation in naturally ventilated buildings in composite climate of India. Building and Environment, 86, 17–28. https://doi.org/10.1016/J.BUILDENV.2014.11.024
12 | ROM Udrea | Romania | Udrea, I., Croitoru, C., Nastase, I., Crutescu, R., & Badescu, V. (2018). First adaptive thermal comfort equation for naturally ventilated buildings in Bucharest, Romania. International Journal of Ventilation, 17(3), 149–165. https://doi.org/10.1080/14733315.2017.1356057
13 | AUS Williamson | Australia | Williamson, T., & Daniel, L. (2020). A new adaptive thermal comfort model for homes in temperate climates of Australia. Energy and Buildings, 210, 109728. https://doi.org/10.1016/j.enbuild.2019.109728
14 | AUS DeDear | Australia | de Dear, R., Kim, J., & Parkinson, T. (2018). Residential adaptive comfort in a humid subtropical climate—Sydney Australia. Energy and Buildings, 158, 1296–1305. https://doi.org/10.1016/j.enbuild.2017.11.028
15 | BRA Rupp NV | Brazil | Rupp, R. F., de Dear, R., & Ghisi, E. (2018). Field study of mixed-mode office buildings in Southern Brazil using an adaptive thermal comfort framework. Energy and Buildings, 158, 1475–1486. https://doi.org/10.1016/J.ENBUILD.2017.11.047
16 | BRA Rupp AC | Brazil | Rupp, R. F., de Dear, R., & Ghisi, E. (2018). Field study of mixed-mode office buildings in Southern Brazil using an adaptive thermal comfort framework. Energy and Buildings, 158, 1475–1486. https://doi.org/10.1016/J.ENBUILD.2017.11.047
17 | MEX Oropeza Arid | Mexico | I. Oropeza-Perez, A.H. Petzold-Rodriguez, C. Bonilla-Lopez, Adaptive thermal comfort in the main Mexican climate conditions with and without passive cooling, Energy and Buildings. 145 (2017) 251–258. https://doi.org/10.1016/j.enbuild.2017.04.031.
18 | MEX Oropeza DryTropic | Mexico | I. Oropeza-Perez, A.H. Petzold-Rodriguez, C. Bonilla-Lopez, Adaptive thermal comfort in the main Mexican climate conditions with and without passive cooling, Energy and Buildings. 145 (2017) 251–258. https://doi.org/10.1016/j.enbuild.2017.04.031.
19 | MEX Oropeza Temperate | Mexico | I. Oropeza-Perez, A.H. Petzold-Rodriguez, C. Bonilla-Lopez, Adaptive thermal comfort in the main Mexican climate conditions with and without passive cooling, Energy and Buildings. 145 (2017) 251–258. https://doi.org/10.1016/j.enbuild.2017.04.031.
20 | MEX Oropeza HumTropic | Mexico | I. Oropeza-Perez, A.H. Petzold-Rodriguez, C. Bonilla-Lopez, Adaptive thermal comfort in the main Mexican climate conditions with and without passive cooling, Energy and Buildings. 145 (2017) 251–258. https://doi.org/10.1016/j.enbuild.2017.04.031.
21 | CHL Perez-Fargallo | Chile | A. Pérez-Fargallo, J.A. Pulido-Arcas, C. Rubio-Bellido, M. Trebilcock, B. Piderit, S. Attia, Development of a new adaptive comfort model for low income housing in the central-south of chile, Energy Build. 178 (2018) 94–106. https://doi.org/10.1016/j.enbuild.2018.08.030.
22 | INT ISO7730 | Worldwide | ISO, 2005. ISO 7730: Ergonomics of the thermal environment Analytical determination and interpretation of thermal comfort using calculation of the PMV and PPD indices and local thermal comfort criteria. Management 3, 605–615. https://doi.org/10.1016/j.soildyn.2004.11.005

## References_paper
ComfStand No. | ComfStand Name | Area | Reference | Reference
0 | CTE | Spain |  | The Government of Spain. Royal Decree 314/2006. Approving the Spanish Technical Building Code CTE-DB-HE-1 2013:1–43. https://www.boe.es/eli/es/rd/2006/03/17/314 (accessed August 6, 2021).
1 | EN16798-1 | Europe |  | European committee for standardization. EN 16798-1:2019 Energy performance of buildings. Ventilation for buildings. Indoor environmental input parameters for design and assessment of energy performance of buildings addressing indoor air quality, thermal environment, lighting and acoustics. 2019. https://en.tienda.aenor.com/norma-bsi-bs-en-16798-1-2019-000000000030297474 (accessed August 6, 2021).
2 | ASHRAE 55 | Worldwide |  | ASHRAE Standard 55-2020 Thermal Environmental Conditions for Human Occupancy, ASHRAE Standard (2020).
3 | JPN·Rijal | Japan |  | Rijal, H. B., Humphreys, M. A., & Nicol, J. F. (2019). Adaptive model and the adaptive mechanisms for thermal comfort in Japanese dwellings. Energy and Buildings, 202, 109371. https://doi.org/10.1016/j.enbuild.2019.109371
4 | GBT50785·Cold | China |  | MOHURD, Evaluation Standard for Indoor Thermal Environment in Civil Buildings (GB/T 50785-2012), Ministry of Housing and Urban-Rural Development (MOHURD), Beijing, China, 2012.
5 | GBT50785·HotMild | China |  | MOHURD, Evaluation Standard for Indoor Thermal Environment in Civil Buildings (GB/T 50785-2012), Ministry of Housing and Urban-Rural Development (MOHURD), Beijing, China, 2012.
6 | CHN·Yang | China |  | Yang, L., Fu, R., He, W., He, Q., & Liu, Y. (2020). Adaptive thermal comfort and climate responsive building design strategies in dry–hot and dry–cold areas: Case study in Turpan, China. Energy and Buildings, 209, 109678. https://doi.org/10.1016/j.enbuild.2019.109678
7 | IMAC·C·NV | India |  | Manu, S., Shukla, Y., Rawal, R., Thomas, L. E., & de Dear, R. (2016). Field studies of thermal comfort across multiple climate zones for the subcontinent: India Model for Adaptive Comfort (IMAC). Building and Environment, 98, 55–70. https://doi.org/10.1016/j.buildenv.2015.12.019
8 | IMAC·C·MM | India |  | Manu, S., Shukla, Y., Rawal, R., Thomas, L. E., & de Dear, R. (2016). Field studies of thermal comfort across multiple climate zones for the subcontinent: India Model for Adaptive Comfort (IMAC). Building and Environment, 98, 55–70. https://doi.org/10.1016/j.buildenv.2015.12.019
9 | IMAC·R·7DRM | India |  | Rawal, R., Shukla, Y., Vardhan, V., Asrani, S., Schweiker, M., de Dear, R., Garg, V., Mathur, J., Prakash, S., Diddi, S., Ranjan, S. V., Siddiqui, A. N., & Somani, G. (2022). Adaptive thermal comfort model based on field studies in five climate zones across India. Building and Environment, 219, 109187. https://doi.org/10.1016/J.BUILDENV.2022.109187
10 | IMAC·R·30DRM | India |  | Rawal, R., Shukla, Y., Vardhan, V., Asrani, S., Schweiker, M., de Dear, R., Garg, V., Mathur, J., Prakash, S., Diddi, S., Ranjan, S. V., Siddiqui, A. N., & Somani, G. (2022). Adaptive thermal comfort model based on field studies in five climate zones across India. Building and Environment, 219, 109187. https://doi.org/10.1016/J.BUILDENV.2022.109187
11 | IND·Dhaka | India |  | Dhaka, S., Mathur, J., Brager, G., & Honnekeri, A. (2015). Assessment of thermal environmental conditions and quantification of thermal adaptation in naturally ventilated buildings in composite climate of India. Building and Environment, 86, 17–28. https://doi.org/10.1016/J.BUILDENV.2014.11.024
12 | ROM·Udrea | Romania |  | Udrea, I., Croitoru, C., Nastase, I., Crutescu, R., & Badescu, V. (2018). First adaptive thermal comfort equation for naturally ventilated buildings in Bucharest, Romania. International Journal of Ventilation, 17(3), 149–165. https://doi.org/10.1080/14733315.2017.1356057
13 | AUS·Williamson | Australia |  | Williamson, T., & Daniel, L. (2020). A new adaptive thermal comfort model for homes in temperate climates of Australia. Energy and Buildings, 210, 109728. https://doi.org/10.1016/j.enbuild.2019.109728
14 | AUS·DeDear | Australia |  | de Dear, R., Kim, J., & Parkinson, T. (2018). Residential adaptive comfort in a humid subtropical climate—Sydney Australia. Energy and Buildings, 158, 1296–1305. https://doi.org/10.1016/j.enbuild.2017.11.028
15 | BRA·Rupp·NV | Brazil |  | Rupp, R. F., de Dear, R., & Ghisi, E. (2018). Field study of mixed-mode office buildings in Southern Brazil using an adaptive thermal comfort framework. Energy and Buildings, 158, 1475–1486. https://doi.org/10.1016/J.ENBUILD.2017.11.047
16 | BRA·Rupp·AC | Brazil |  | Rupp, R. F., de Dear, R., & Ghisi, E. (2018). Field study of mixed-mode office buildings in Southern Brazil using an adaptive thermal comfort framework. Energy and Buildings, 158, 1475–1486. https://doi.org/10.1016/J.ENBUILD.2017.11.047

## References (2)
ComfStand No. | ComfStand Name | Area | Reference
0 | CTE | Spain | The Government of Spain. Royal Decree 314/2006. Approving the Spanish Technical Building Code CTE-DB-HE-1 2013:1–43. https://www.boe.es/eli/es/rd/2006/03/17/314 (accessed August 6, 2021). | ComfStand No.: 0; ComfStand Name: CTE; Area: Spain; Reference: The Government of Spain. Royal Decree 314/2006. Approving the Spanish Technical Building Code CTE-DB-HE-1 2013:1–43. https://www.boe.es/eli/es/rd/2006/03/17/314 (accessed August 6, 2021).
1 | EN16798-1 | Europe | European committee for standardization. EN 16798-1:2019 Energy performance of buildings. Ventilation for buildings. Indoor environmental input parameters for design and assessment of energy performance of buildings addressing indoor air quality, thermal environment, lighting and acoustics. 2019. https://en.tienda.aenor.com/norma-bsi-bs-en-16798-1-2019-000000000030297474 (accessed August 6, 2021). | ComfStand No.: 1; ComfStand Name: EN16798-1; Area: Europe; Reference: European committee for standardization. EN 16798-1:2019 Energy performance of buildings. Ventilation for buildings. Indoor environmental input parameters for design and assessment of energy performance of buildings addressing indoor air quality, thermal environment, lighting and acoustics. 2019. https://en.tienda.aenor.com/norma-bsi-bs-en-16798-1-2019-000000000030297474 (accessed August 6, 2021).
2 | ASHRAE 55 | Worldwide | ASHRAE Standard 55-2020 Thermal Environmental Conditions for Human Occupancy, ASHRAE Standard (2020). | ComfStand No.: 2; ComfStand Name: ASHRAE 55; Area: Worldwide; Reference: ASHRAE Standard 55-2020 Thermal Environmental Conditions for Human Occupancy, ASHRAE Standard (2020).
3 | JPN·Rijal | Japan | Rijal, H. B., Humphreys, M. A., & Nicol, J. F. (2019). Adaptive model and the adaptive mechanisms for thermal comfort in Japanese dwellings. Energy and Buildings, 202, 109371. https://doi.org/10.1016/j.enbuild.2019.109371 | ComfStand No.: 3; ComfStand Name: JPN·Rijal; Area: Japan; Reference: Rijal, H. B., Humphreys, M. A., & Nicol, J. F. (2019). Adaptive model and the adaptive mechanisms for thermal comfort in Japanese dwellings. Energy and Buildings, 202, 109371. https://doi.org/10.1016/j.enbuild.2019.109371
4 | GBT50785·Cold | China | MOHURD, Evaluation Standard for Indoor Thermal Environment in Civil Buildings (GB/T 50785-2012), Ministry of Housing and Urban-Rural Development (MOHURD), Beijing, China, 2012. | ComfStand No.: 4; ComfStand Name: GBT50785·Cold; Area: China; Reference: MOHURD, Evaluation Standard for Indoor Thermal Environment in Civil Buildings (GB/T 50785-2012), Ministry of Housing and Urban-Rural Development (MOHURD), Beijing, China, 2012.
5 | GBT50785·HotMild | China | MOHURD, Evaluation Standard for Indoor Thermal Environment in Civil Buildings (GB/T 50785-2012), Ministry of Housing and Urban-Rural Development (MOHURD), Beijing, China, 2012. | ComfStand No.: 5; ComfStand Name: GBT50785·HotMild; Area: China; Reference: MOHURD, Evaluation Standard for Indoor Thermal Environment in Civil Buildings (GB/T 50785-2012), Ministry of Housing and Urban-Rural Development (MOHURD), Beijing, China, 2012.
6 | CHN·Yang | China | Yang, L., Fu, R., He, W., He, Q., & Liu, Y. (2020). Adaptive thermal comfort and climate responsive building design strategies in dry–hot and dry–cold areas: Case study in Turpan, China. Energy and Buildings, 209, 109678. https://doi.org/10.1016/j.enbuild.2019.109678 | ComfStand No.: 6; ComfStand Name: CHN·Yang; Area: China; Reference: Yang, L., Fu, R., He, W., He, Q., & Liu, Y. (2020). Adaptive thermal comfort and climate responsive building design strategies in dry–hot and dry–cold areas: Case study in Turpan, China. Energy and Buildings, 209, 109678. https://doi.org/10.1016/j.enbuild.2019.109678
7 | IMAC·C·NV | India | Manu, S., Shukla, Y., Rawal, R., Thomas, L. E., & de Dear, R. (2016). Field studies of thermal comfort across multiple climate zones for the subcontinent: India Model for Adaptive Comfort (IMAC). Building and Environment, 98, 55–70. https://doi.org/10.1016/j.buildenv.2015.12.019 | ComfStand No.: 7; ComfStand Name: IMAC·C·NV; Area: India; Reference: Manu, S., Shukla, Y., Rawal, R., Thomas, L. E., & de Dear, R. (2016). Field studies of thermal comfort across multiple climate zones for the subcontinent: India Model for Adaptive Comfort (IMAC). Building and Environment, 98, 55–70. https://doi.org/10.1016/j.buildenv.2015.12.019
8 | IMAC·C·MM | India | Manu, S., Shukla, Y., Rawal, R., Thomas, L. E., & de Dear, R. (2016). Field studies of thermal comfort across multiple climate zones for the subcontinent: India Model for Adaptive Comfort (IMAC). Building and Environment, 98, 55–70. https://doi.org/10.1016/j.buildenv.2015.12.019 | ComfStand No.: 8; ComfStand Name: IMAC·C·MM; Area: India; Reference: Manu, S., Shukla, Y., Rawal, R., Thomas, L. E., & de Dear, R. (2016). Field studies of thermal comfort across multiple climate zones for the subcontinent: India Model for Adaptive Comfort (IMAC). Building and Environment, 98, 55–70. https://doi.org/10.1016/j.buildenv.2015.12.019
9 | IMAC·R·7DRM | India | Rawal, R., Shukla, Y., Vardhan, V., Asrani, S., Schweiker, M., de Dear, R., Garg, V., Mathur, J., Prakash, S., Diddi, S., Ranjan, S. V., Siddiqui, A. N., & Somani, G. (2022). Adaptive thermal comfort model based on field studies in five climate zones across India. Building and Environment, 219, 109187. https://doi.org/10.1016/J.BUILDENV.2022.109187 | ComfStand No.: 9; ComfStand Name: IMAC·R·7DRM; Area: India; Reference: Rawal, R., Shukla, Y., Vardhan, V., Asrani, S., Schweiker, M., de Dear, R., Garg, V., Mathur, J., Prakash, S., Diddi, S., Ranjan, S. V., Siddiqui, A. N., & Somani, G. (2022). Adaptive thermal comfort model based on field studies in five climate zones across India. Building and Environment, 219, 109187. https://doi.org/10.1016/J.BUILDENV.2022.109187
10 | IMAC·R·30DRM | India | Rawal, R., Shukla, Y., Vardhan, V., Asrani, S., Schweiker, M., de Dear, R., Garg, V., Mathur, J., Prakash, S., Diddi, S., Ranjan, S. V., Siddiqui, A. N., & Somani, G. (2022). Adaptive thermal comfort model based on field studies in five climate zones across India. Building and Environment, 219, 109187. https://doi.org/10.1016/J.BUILDENV.2022.109187 | ComfStand No.: 10; ComfStand Name: IMAC·R·30DRM; Area: India; Reference: Rawal, R., Shukla, Y., Vardhan, V., Asrani, S., Schweiker, M., de Dear, R., Garg, V., Mathur, J., Prakash, S., Diddi, S., Ranjan, S. V., Siddiqui, A. N., & Somani, G. (2022). Adaptive thermal comfort model based on field studies in five climate zones across India. Building and Environment, 219, 109187. https://doi.org/10.1016/J.BUILDENV.2022.109187
11 | IND·Dhaka | India | Dhaka, S., Mathur, J., Brager, G., & Honnekeri, A. (2015). Assessment of thermal environmental conditions and quantification of thermal adaptation in naturally ventilated buildings in composite climate of India. Building and Environment, 86, 17–28. https://doi.org/10.1016/J.BUILDENV.2014.11.024 | ComfStand No.: 11; ComfStand Name: IND·Dhaka; Area: India; Reference: Dhaka, S., Mathur, J., Brager, G., & Honnekeri, A. (2015). Assessment of thermal environmental conditions and quantification of thermal adaptation in naturally ventilated buildings in composite climate of India. Building and Environment, 86, 17–28. https://doi.org/10.1016/J.BUILDENV.2014.11.024
12 | ROM·Udrea | Romania | Udrea, I., Croitoru, C., Nastase, I., Crutescu, R., & Badescu, V. (2018). First adaptive thermal comfort equation for naturally ventilated buildings in Bucharest, Romania. International Journal of Ventilation, 17(3), 149–165. https://doi.org/10.1080/14733315.2017.1356057 | ComfStand No.: 12; ComfStand Name: ROM·Udrea; Area: Romania; Reference: Udrea, I., Croitoru, C., Nastase, I., Crutescu, R., & Badescu, V. (2018). First adaptive thermal comfort equation for naturally ventilated buildings in Bucharest, Romania. International Journal of Ventilation, 17(3), 149–165. https://doi.org/10.1080/14733315.2017.1356057
13 | AUS·Williamson | Australia | Williamson, T., & Daniel, L. (2020). A new adaptive thermal comfort model for homes in temperate climates of Australia. Energy and Buildings, 210, 109728. https://doi.org/10.1016/j.enbuild.2019.109728 | ComfStand No.: 13; ComfStand Name: AUS·Williamson; Area: Australia; Reference: Williamson, T., & Daniel, L. (2020). A new adaptive thermal comfort model for homes in temperate climates of Australia. Energy and Buildings, 210, 109728. https://doi.org/10.1016/j.enbuild.2019.109728
14 | AUS·DeDear | Australia | de Dear, R., Kim, J., & Parkinson, T. (2018). Residential adaptive comfort in a humid subtropical climate—Sydney Australia. Energy and Buildings, 158, 1296–1305. https://doi.org/10.1016/j.enbuild.2017.11.028 | ComfStand No.: 14; ComfStand Name: AUS·DeDear; Area: Australia; Reference: de Dear, R., Kim, J., & Parkinson, T. (2018). Residential adaptive comfort in a humid subtropical climate—Sydney Australia. Energy and Buildings, 158, 1296–1305. https://doi.org/10.1016/j.enbuild.2017.11.028
15 | BRA·Rupp·NV | Brazil | Rupp, R. F., de Dear, R., & Ghisi, E. (2018). Field study of mixed-mode office buildings in Southern Brazil using an adaptive thermal comfort framework. Energy and Buildings, 158, 1475–1486. https://doi.org/10.1016/J.ENBUILD.2017.11.047 | ComfStand No.: 15; ComfStand Name: BRA·Rupp·NV; Area: Brazil; Reference: Rupp, R. F., de Dear, R., & Ghisi, E. (2018). Field study of mixed-mode office buildings in Southern Brazil using an adaptive thermal comfort framework. Energy and Buildings, 158, 1475–1486. https://doi.org/10.1016/J.ENBUILD.2017.11.047
16 | BRA·Rupp·AC | Brazil | Rupp, R. F., de Dear, R., & Ghisi, E. (2018). Field study of mixed-mode office buildings in Southern Brazil using an adaptive thermal comfort framework. Energy and Buildings, 158, 1475–1486. https://doi.org/10.1016/J.ENBUILD.2017.11.047 | ComfStand No.: 16; ComfStand Name: BRA·Rupp·AC; Area: Brazil; Reference: Rupp, R. F., de Dear, R., & Ghisi, E. (2018). Field study of mixed-mode office buildings in Southern Brazil using an adaptive thermal comfort framework. Energy and Buildings, 158, 1475–1486. https://doi.org/10.1016/J.ENBUILD.2017.11.047