## Equations
ComfStand |  | CAT | ComfMod | PMV-based model when adaptive is not applicable | Season / Climate zone | Cooling setpoint temperature (°C) |  |  | Heating setpoint temperature (°C)
[6 empty] | WMOT < ACSTall | ACSTall < WMOT < ACSTaul | ACSTaul < WMOT | WMOT < AHSTall | AHSTall < WMOT < AHSTaul | AHSTaul < WMOT
0 | CTE | NA | NA |  |  | 23:00-08:00h: 27 / 08:00-23:00h: 25 |  |  | 23:00-08:00h: 17 / 08:00-23:00h: 20
1 | INT EN16798-1 | 1 | 0 |  | SS | 25.5 |  |  | 23.5
[5 empty] | WS | 25 |  |  | 21
|  |  | 1 | Spanish Building Code | All | 27-25 | RMOT*0.33+18.8+2 | 27-25 | 17-20 | RMOT*0.33+18.8-3 | 17-20
|  |  | 2 | EN16798-1 Static | All | 25 | RMOT*0.33+18.8+2 | 25.5 | 21 | RMOT*0.33+18.8-3 | 23.5
|  |  | 3 | Adap. Limits Horizont. Extended | All | 10*0.33+18.8+2 | RMOT*0.33+18.8+2 | 30*0.33+18.8+2 | 10*0.33+18.8-3 | RMOT*0.33+18.8-3 | 30*0.33+18.8-3
|  | 2 | 0 |  | SS | 26 |  |  | 23
[5 empty] | WS | 25 |  |  | 20
|  |  | 1 | Spanish Building Code | All | 27-25 | RMOT*0.33+18.8+3 | 27-25 | 17-20 | RMOT*0.33+18.8-4 | 17-20
|  |  | 2 | EN16798-1 Static | All | 25 | RMOT*0.33+18.8+3 | 26 | 20 | RMOT*0.33+18.8-4 | 23
|  |  | 3 | Adap. Limits Horizont. Extended | All | 10*0.33+18.8+3 | RMOT*0.33+18.8+3 | 30*0.33+18.8+3 | 10*0.33+18.8-4 | RMOT*0.33+18.8-4 | 30*0.33+18.8-4
|  | 3 | 0 |  | SS | 27 |  |  | 22
[5 empty] | WS | 25 |  |  | 18
|  |  | 1 | Spanish Building Code | All | 27-25 | RMOT*0.33+18.8+4 | 27-25 | 17-20 | RMOT*0.33+18.8-5 | 17-20
|  |  | 2 | EN16798-1 Static | All | 25 | RMOT*0.33+18.8+4 | 27 | 18 | RMOT*0.33+18.8-5 | 22
|  |  | 3 | Adap. Limits Horizont. Extended | All | 10*0.33+18.8+4 | RMOT*0.33+18.8+4 | 30*0.33+18.8+4 | 10*0.33+18.8-5 | RMOT*0.33+18.8-5 | 30*0.33+18.8-5
2 | INT ASHRAE55 | 80 | 0 |  | SS | 27 |  |  | 22
[5 empty] | WS | 25 |  |  | 19
|  |  | 1 | CTE | All | 27-25 | PMOT*0.31+17.8+3.5 | 27-25 | 17-20 | PMOT*0.31+17.8-3.5 | 17-20
|  |  | 2 | ISO 7730 | All | 25 | PMOT*0.31+17.8+3.5 | 27 | 19 | PMOT*0.31+17.8-3.5 | 22
|  |  | 3 | Adap. Limits Horizont. Extended | All | 10*0.31+17.8+3.5 | PMOT*0.31+17.8+3.5 | 33.5*0.31+17.8+3.5 | 10*0.31+17.8-3.5 | PMOT*0.31+17.8-3.5 | 33.5*0.31+17.8-3.5
|  | 90 | 0 |  | SS | 26 |  |  | 23
[5 empty] | WS | 24 |  |  | 20
|  |  | 1 | CTE | All | 27-25 | PMOT*0.31+17.8+2.5 | 27-25 | 17-20 | PMOT*0.31+17.8-2.5 | 17-20
|  |  | 2 | ISO 7730 | All | 24 | PMOT*0.31+17.8+2.5 | 26 | 20 | PMOT*0.31+17.8-2.5 | 23
|  |  | 3 | Adap. Limits Horizont. Extended | All | 10*0.31+17.8+2.5 | PMOT*0.31+17.8+2.5 | 33.5*0.31+17.8+2.5 | 10*0.31+17.8-2.5 | PMOT*0.31+17.8-2.5 | 33.5*0.31+17.8-2.5
3 | JPN Rijal | 80 | 0 |  | All | 28 |  |  | 18
|  |  | 1 | COOLBIZ | All | 28 | PMOT*0.48+14.4+3.5 | 28 | 18 | PMOT*0.48+14.4-3.5 | 18
|  |  | 2 | ISO 7730 | All | 25 | PMOT*0.48+14.4+3.5 | 27 | 19 | PMOT*0.48+14.4-3.5 | 22
|  |  | 3 | Adap. Limits Horizont. Extended | All | 5*0.48+14.4+3.5 | PMOT*0.48+14.4+3.5 | 30*0.48+14.4+3.5 | 5*0.48+14.4-3.5 | PMOT*0.48+14.4-3.5 | 30*0.48+14.4-3.5
|  | 90 | 0 |  | All | 27 |  |  | 19
|  |  | 1 | COOLBIZ | All | 27 | PMOT*0.48+14.4+2.5 | 27 | 19 | PMOT*0.48+14.4-2.5 | 19
|  |  | 2 | ISO 7730 | All | 24 | PMOT*0.48+14.4+2.5 | 26 | 20 | PMOT*0.48+14.4-2.5 | 23
|  |  | 3 | Adap. Limits Horizont. Extended | All | 5*0.48+14.4+2.5 | PMOT*0.48+14.4+2.5 | 30*0.48+14.4+2.5 | 5*0.48+14.4-2.5 | PMOT*0.48+14.4-2.5 | 30*0.48+14.4-2.5
4 | CHN GB/T 50785 - Cold | 1 (90%) | - | Adap. Limits Horizont. Extended | All | 18*0.77+12.04 | PMOT*0.77+12.04 | 28*0.77+12.04 | 18*0.87+2.76 | PMOT*0.87+2.76 | 28*0.87+2.76
|  | 2 (75-90%) | - | Adap. Limits Horizont. Extended | All | 18*0.73+15.28 | PMOT*0.73+15.28 | 30*0.73+15.28 | 16*0.91-0.48 | PMOT*0.91-0.48 | 28*0.91-0.48
5 | CHN GB/T 50785 - Hot & Mild | 1 (90%) | - | Adap. Limits Horizont. Extended | All | 18*0.77+9.34 | PMOT*0.77+9.34 | 28*0.77+9.34 | 18*0.87-0.31 | PMOT*0.87-0.31 | 28*0.87-0.31
|  | 2 (75-90%) | - | Adap. Limits Horizont. Extended | All | 18*0.73+12.72 | PMOT*0.73+12.72 | 30*0.73+12.72 | 16*0.91-3.69 | PMOT*0.91-3.69 | 28*0.91-3.69
6 | CHN Yang | 80 | 0 |  | All | ? |  |  | ?
|  |  | 1 |  | All | ? | ? | ? | ? | ? | ?
|  |  | 2 | ISO 7730 | All | 25 | PMOT*0.30+25.9 | 27 | 19 | PMOT*0.32+14.88 | 22
|  |  | 3 | Adap. Limits Horizont. Extended | All | -7*0.30+25.9 | PMOT*0.30+25.9 | 30*0.30+25.9 | -7*0.32+14.88 | PMOT*0.32+14.88 | 30*0.32+14.88
|  | 90 | 0 |  | All | ? |  |  | ?
|  |  | 1 |  | All | ? | ? | ? | ? | ? | ?
|  |  | 2 | ISO 7730 | All | 24 | PMOT*0.30+23.6 | 26 | 20 | PMOT*0.31+17.14 | 23
|  |  | 3 | Adap. Limits Horizont. Extended | All | -7*0.30+23.6 | PMOT*0.30+23.6 | 30*0.30+23.6 | -7*0.31+17.14 | PMOT*0.31+17.14 | 30*0.31+17.14
7 | IND IMAC C NV | 80 | 0 |  | All | PMOT*0.078+23.25+2.72 | PMOT*0.078+23.25+1 | PMOT*0.078+23.25+1 | PMOT*0.078+23.25-2.72 | PMOT*0.078+23.25-1 | PMOT*0.078+23.25-1
|  |  | 1 | Indian Building Code | All | PMOT*0.078+23.25+2.72 | PMOT*0.54+12.83+4.1 | PMOT*0.078+23.25+2.72 | PMOT*0.078+23.25-2.72 | PMOT*0.54+12.83-4.1 | PMOT*0.078+23.25-2.72
|  |  | 2 | ISO 7730 | All | 25 | PMOT*0.54+12.83+4.1 | 27 | 19 | PMOT*0.54+12.83-4.1 | 22
|  |  | 3 | Adap. Limits Horizont. Extended | All | 12.5*0.54+12.83+4.1 | PMOT*0.54+12.83+4.1 | 31*0.54+12.83+4.1 | 12.5*0.54+12.83-4.1 | PMOT*0.54+12.83-4.1 | 31*0.54+12.83-4.1
|  | 85 | 0 |  | All | PMOT*0.078+23.25+2.11 | PMOT*0.078+23.25+3.3 | PMOT*0.078+23.25+3.3 | PMOT*0.078+23.25-2.11 | PMOT*0.078+23.25-3.3 | PMOT*0.078+23.25-3.3
|  |  | 1 | Indian Building Code | All | PMOT*0.078+23.25+2.11 | PMOT*0.54+12.83+3.3 | PMOT*0.078+23.25+2.11 | PMOT*0.078+23.25-2.11 | PMOT*0.54+12.83-3.3 | PMOT*0.078+23.25-2.11
|  |  | 2 | ISO 7730 | All | 24.5 | PMOT*0.54+12.83+3.3 | 26.5 | 19.5 | PMOT*0.54+12.83-3.3 | 22.5
|  |  | 3 | Adap. Limits Horizont. Extended | All | 12.5*0.54+12.83+3.3 | PMOT*0.54+12.83+3.3 | 31*0.54+12.83+3.3 | 12.5*0.54+12.83-3.3 | PMOT*0.54+12.83-3.3 | 31*0.54+12.83-3.3
|  | 90 | 0 |  | All | PMOT*0.078+23.25+1.5 | PMOT*0.078+23.25+2.4 | PMOT*0.078+23.25+2.4 | PMOT*0.078+23.25-1.5 | PMOT*0.078+23.25-2.4 | PMOT*0.078+23.25-2.4
|  |  | 1 | Indian Building Code | All | PMOT*0.078+23.25+1.5 | PMOT*0.54+12.83+2.4 | PMOT*0.078+23.25+1.5 | PMOT*0.078+23.25-1.5 | PMOT*0.54+12.83-2.4 | PMOT*0.078+23.25-1.5
|  |  | 2 | ISO 7730 | All | 24 | PMOT*0.54+12.83+2.4 | 26 | 20 | PMOT*0.54+12.83-2.4 | 23
|  |  | 3 | Adap. Limits Horizont. Extended | All | 12.5*0.54+12.83+2.4 | PMOT*0.54+12.83+2.4 | 31*0.54+12.83+2.4 | 12.5*0.54+12.83-2.4 | PMOT*0.54+12.83-2.4 | 31*0.54+12.83-2.4
8 | IND IMAC C MM | 80 | 0 |  | All | PMOT*0.078+23.25+2.72 | PMOT*0.078+23.25+5.9 | PMOT*0.078+23.25+5.9 | PMOT*0.078+23.25-2.72 | PMOT*0.078+23.25-5.9 | PMOT*0.078+23.25-5.9
|  |  | 1 | Indian Building Code | All | PMOT*0.078+23.25+2.72 | PMOT*0.28+17.87+5.9 | PMOT*0.078+23.25+2.72 | PMOT*0.078+23.25-2.72 | PMOT*0.28+17.87-5.9 | PMOT*0.078+23.25-2.72
|  |  | 2 | ISO 7730 | All | 25 | PMOT*0.28+17.87+5.9 | 27 | 19 | PMOT*0.28+17.87-5.9 | 22
|  |  | 3 | Adap. Limits Horizont. Extended | All | 13*0.28+17.87+5.9 | PMOT*0.28+17.87+5.9 | 38.5*0.28+17.87+5.9 | 13*0.28+17.87-5.9 | PMOT*0.28+17.87-5.9 | 38.5*0.28+17.87-5.9
|  | 85 | 0 |  | All | PMOT*0.078+23.25+2.11 | PMOT*0.078+23.25+4.8 | PMOT*0.078+23.25+4.8 | PMOT*0.078+23.25-2.11 | PMOT*0.078+23.25-4.8 | PMOT*0.078+23.25-4.8
|  |  | 1 | Indian Building Code | All | PMOT*0.078+23.25+2.11 | PMOT*0.28+17.87+4.8 | PMOT*0.078+23.25+2.11 | PMOT*0.078+23.25-2.11 | PMOT*0.28+17.87-4.8 | PMOT*0.078+23.25-2.11
|  |  | 2 | ISO 7730 | All | 24.5 | PMOT*0.28+17.87+4.8 | 26.5 | 19.5 | PMOT*0.28+17.87-4.8 | 22.5
|  |  | 3 | Adap. Limits Horizont. Extended | All | 13*0.28+17.87+4.8 | PMOT*0.28+17.87+4.8 | 38.5*0.28+17.87+4.8 | 13*0.28+17.87-4.8 | PMOT*0.28+17.87-4.8 | 38.5*0.28+17.87-4.8
|  | 90 | 0 |  | All | PMOT*0.078+23.25+1.5 | PMOT*0.078+23.25+3.5 | PMOT*0.078+23.25+3.5 | PMOT*0.078+23.25-1.5 | PMOT*0.078+23.25-3.5 | PMOT*0.078+23.25-3.5
|  |  | 1 | Indian Building Code | All | PMOT*0.078+23.25+1.5 | PMOT*0.28+17.87+3.5 | PMOT*0.078+23.25+1.5 | PMOT*0.078+23.25-1.5 | PMOT*0.28+17.87-3.5 | PMOT*0.078+23.25-1.5
|  |  | 2 | ISO 7730 | All | 24 | PMOT*0.28+17.87+3.5 | 26 | 20 | PMOT*0.28+17.87-3.5 | 23
|  |  | 3 | Adap. Limits Horizont. Extended | All | 13*0.28+17.87+3.5 | PMOT*0.28+17.87+3.5 | 38.5*0.28+17.87+3.5 | 13*0.28+17.87-3.5 | PMOT*0.28+17.87-3.5 | 38.5*0.28+17.87-3.5
9 | IND IMAC R 7DRM | 80 | 0 |  | All | PMOT*0.078+23.25+2.72 | PMOT*0.078+23.25+3.6 | PMOT*0.078+23.25+3.6 | PMOT*0.078+23.25-2.72 | PMOT*0.078+23.25-3.6 | PMOT*0.078+23.25-3.6
|  |  | 1 | Indian Building Code | All | PMOT*0.078+23.25+2.72 | PMOT*0.39+18.42+3.6 | PMOT*0.078+23.25+2.72 | PMOT*0.078+23.25-2.72 | PMOT*0.39+18.42-3.6 | PMOT*0.078+23.25-2.72
|  |  | 2 | ISO 7730 | All | 25 | PMOT*0.39+18.42+3.6 | 27 | 19 | PMOT*0.39+18.42-3.6 | 22
|  |  | 3 | Adap. Limits Horizont. Extended | All | 5.5*0.39+18.42+3.6 | PMOT*0.39+18.42+3.6 | 33*0.39+18.42+3.6 | 5.5*0.39+18.42-3.6 | PMOT*0.39+18.42-3.6 | 33*0.39+18.42-3.6
|  | 90 | 0 |  | All | PMOT*0.078+23.25+1.5 | PMOT*0.078+23.25+2.15 | PMOT*0.078+23.25+2.15 | PMOT*0.078+23.25-1.5 | PMOT*0.078+23.25-2.15 | PMOT*0.078+23.25-2.15
|  |  | 1 | Indian Building Code | All | PMOT*0.078+23.25+1.5 | PMOT*0.39+18.42+2.15 | PMOT*0.078+23.25+1.5 | PMOT*0.078+23.25-1.5 | PMOT*0.39+18.42-2.15 | PMOT*0.078+23.25-1.5
|  |  | 2 | ISO 7730 | All | 24 | PMOT*0.39+18.42+2.15 | 26 | 20 | PMOT*0.39+18.42-2.15 | 23
|  |  | 3 | Adap. Limits Horizont. Extended | All | 5.5*0.39+18.42+2.15 | PMOT*0.39+18.42+2.15 | 33*0.39+18.42+2.15 | 5.5*0.39+18.42-2.15 | PMOT*0.39+18.42-2.15 | 33*0.39+18.42-2.15
10 | IND IMAC R 30DRM | 80 | 0 |  | All | RMOT*0.078+23.25+2.72 | RMOT*0.078+23.25+3.6 | RMOT*0.078+23.25+3.6 | RMOT*0.078+23.25-2.72 | RMOT*0.078+23.25-3.6 | RMOT*0.078+23.25-3.6
|  |  | 1 | Indian Building Code | All | RMOT*0.078+23.25+2.72 | RMOT*0.42+17.6+3.6 | RMOT*0.078+23.25+2.72 | RMOT*0.078+23.25-2.72 | RMOT*0.42+17.6-3.6 | RMOT*0.078+23.25-2.72
|  |  | 2 | ISO 7730 | All | 25 | RMOT*0.42+17.6+3.6 | 27 | 19 | RMOT*0.42+17.6-3.6 | 22
|  |  | 3 | Adap. Limits Horizont. Extended | All | 5.5*0.42+17.6+3.6 | RMOT*0.42+17.6+3.6 | 33*0.42+17.6+3.6 | 5.5*0.42+17.6-3.6 | RMOT*0.42+17.6-3.6 | 33*0.42+17.6-3.6
|  | 90 | 0 |  | All | RMOT*0.078+23.25+1.5 | RMOT*0.078+23.25+2.15 | RMOT*0.078+23.25+2.15 | RMOT*0.078+23.25-1.5 | RMOT*0.078+23.25-2.15 | RMOT*0.078+23.25-2.15
|  |  | 1 | Indian Building Code | All | RMOT*0.078+23.25+1.5 | RMOT*0.42+17.6+2.15 | RMOT*0.078+23.25+1.5 | RMOT*0.078+23.25-1.5 | RMOT*0.42+17.6-2.15 | RMOT*0.078+23.25-1.5
|  |  | 2 | ISO 7730 | All | 24 | RMOT*0.42+17.6+2.15 | 26 | 20 | RMOT*0.42+17.6-2.15 | 23
|  |  | 3 | Adap. Limits Horizont. Extended | All | 5.5*0.42+17.6+2.15 | RMOT*0.42+17.6+2.15 | 33*0.42+17.6+2.15 | 5.5*0.42+17.6-2.15 | RMOT*0.42+17.6-2.15 | 33*0.42+17.6-2.15
11 | IND Dhaka | 80 | 0 |  | All | RMOT*0.078+23.25+2.72 | RMOT*0.078+23.25+3.5 | RMOT*0.078+23.25+3.5 | RMOT*0.078+23.25-2.72 | RMOT*0.078+23.25-3.5 | RMOT*0.078+23.25-3.5
|  |  | 1 | Indian Building Code | All | RMOT*0.078+23.25+2.72 | RMOT*0.75+5.37+3.5 | RMOT*0.078+23.25+2.72 | RMOT*0.078+23.25-2.72 | RMOT*0.75+5.37-3.5 | RMOT*0.078+23.25-2.72
|  |  | 2 | ISO 7730 | All | 25 | RMOT*0.75+5.37+3.5 | 27 | 19 | RMOT*0.75+5.37-3.5 | 22
|  |  | 3 | Adap. Limits Horizont. Extended | All | ?*0.75+5.37+3.5 | RMOT*0.75+5.37+3.5 | ?*0.75+5.37+3.5 | ?*0.75+5.37-3.5 | RMOT*0.75+5.37-3.5 | ?*0.75+5.37-3.5
|  | 90 | 0 |  | All | RMOT*0.078+23.25+1.5 | RMOT*0.078+23.25+2.5 | RMOT*0.078+23.25+2.5 | RMOT*0.078+23.25-1.5 | RMOT*0.078+23.25-2.5 | RMOT*0.078+23.25-2.5
|  |  | 1 | Indian Building Code | All | RMOT*0.078+23.25+1.5 | RMOT*0.75+5.37+2.5 | RMOT*0.078+23.25+1.5 | RMOT*0.078+23.25-1.5 | RMOT*0.75+5.37-2.5 | RMOT*0.078+23.25-1.5
|  |  | 2 | ISO 7730 | All | 24 | RMOT*0.75+5.37+2.5 | 26 | 20 | RMOT*0.75+5.37-2.5 | 23
|  |  | 3 | Adap. Limits Horizont. Extended | All | ?*0.75+5.37+2.5 | RMOT*0.75+5.37+2.5 | ?*0.75+5.37+2.5 | ?*0.75+5.37-2.5 | RMOT*0.75+5.37-2.5 | ?*0.75+5.37-2.5
12 | ROM Udrea | 80 | 0 |  | All | 27 |  |  | 20
|  |  | 1 | Romanian Building Code | All | 27 | PMOT*0.25+19.7+2.89 | 27 | 20 | PMOT*0.25+19.7-2.89 | 20
|  |  | 2 | ISO 7730 | All | 25 | PMOT*0.25+19.7+2.89 | 27 | 19 | PMOT*0.25+19.7-2.89 | 22
|  |  | 3 | Adap. Limits Horizont. Extended | All | 10*0.25+19.7+2.89 | PMOT*0.25+19.7+2.89 | 33.5*0.25+19.7+2.89 | 10*0.25+19.7-2.89 | PMOT*0.25+19.7-2.89 | 33.5*0.25+19.7-2.89
|  | 90 | 0 |  | All | 25.5 |  |  | 21.5
|  |  | 1 | Romanian Building Code | All | 25.5 | PMOT*0.25+19.7+1.7 | 25.5 | 21.5 | PMOT*0.25+19.7-1.7 | 21.5
|  |  | 2 | ISO 7730 | All | 24 | PMOT*0.25+19.7+1.7 | 26 | 20 | PMOT*0.25+19.7-1.7 | 23
|  |  | 3 | Adap. Limits Horizont. Extended | All | 10*0.25+19.7+1.7 | PMOT*0.25+19.7+1.7 | 33.5*0.25+19.7+1.7 | 10*0.25+19.7-1.7 | PMOT*0.25+19.7-1.7 | 33.5*0.25+19.7-1.7
13 | AUS Williamson | 80 | 0.1 |  | CZ1, 2, 3 | 6:00 to 23:00: 27; else: 24 |  |  | 6:00 to 12:00: 20; else: 18
|  |  | 0.2 |  | CZ4 | 6:00 to 23:00: 26; else: 24 |  |  | 6:00 to 12:00: 20; else: 18
|  |  | 0.3 |  | CZ5 | 6:00 to 23:00: 25; else: 24 |  |  | 6:00 to 12:00: 20; else: 18
|  |  | 0.4 |  | CZ6, 7 | 6:00 to 23:00: 24; else: 24 |  |  | 6:00 to 12:00: 20; else: 18
|  |  | 0.5 |  | CZ8 | 6:00 to 23:00: 23; else: 24 |  |  | 6:00 to 12:00: 20; else: 18
|  |  | 1.1 | Australian Building Code | CZ1, 2, 3 | 6 to 23h: 27; else: 24 | RMOT*0.26+15.9+4.55 | 6 to 23h: 27; else: 24 | 6 to 12am: 20; else: 18 | RMOT*0.26+15.9-4.55 | 6 to 12am: 20; else: 18
|  |  | 1.2 | Australian Building Code | CZ4 | 6 to 23h: 26; else: 24 | RMOT*0.26+15.9+4.55 | 6 to 23h: 26; else: 24 | 6 to 12am: 20; else: 18 | RMOT*0.26+15.9-4.55 | 6 to 12am: 20; else: 18
|  |  | 1.3 | Australian Building Code | CZ5 | 6 to 23h: 25; else: 24 | RMOT*0.26+15.9+4.55 | 6 to 23h: 25; else: 24 | 6 to 12am: 20; else: 18 | RMOT*0.26+15.9-4.55 | 6 to 12am: 20; else: 18
|  |  | 1.4 | Australian Building Code | CZ6, 7 | 6 to 23h: 24; else: 24 | RMOT*0.26+15.9+4.55 | 6 to 23h: 24; else: 24 | 6 to 12am: 20; else: 18 | RMOT*0.26+15.9-4.55 | 6 to 12am: 20; else: 18
|  |  | 1.5 | Australian Building Code | CZ8 | 6 to 23h: 23; else: 24 | RMOT*0.26+15.9+4.55 | 6 to 23h: 23; else: 24 | 6 to 12am: 20; else: 18 | RMOT*0.26+15.9-4.55 | 6 to 12am: 20; else: 18
|  |  | 2 | ISO 7730 | All | 25 | RMOT*0.26+15.9+4.55 | 27 | 19 | RMOT*0.26+15.9-4.55 | 22
|  |  | 3 | Adap. Limits Horizont. Extended | All | 10*0.26+15.9+4.55 | RMOT*0.26+15.9+4.55 | 25*0.26+15.9+4.55 | 10*0.26+15.9-4.55 | RMOT*0.26+15.9-4.55 | 25*0.26+15.9-4.55
|  | 90 | 0.1 |  | CZ1, 2, 3 | 6:00 to 23:00: 26; else: 23 |  |  | 6:00 to 12:00: 21; else: 19
|  |  | 0.2 |  | CZ4 | 6:00 to 23:00: 25; else: 23 |  |  | 6:00 to 12:00: 21; else: 19
|  |  | 0.3 |  | CZ5 | 6:00 to 23:00: 24; else: 23 |  |  | 6:00 to 12:00: 21; else: 19
|  |  | 0.4 |  | CZ6, 7 | 6:00 to 23:00: 23; else: 23 |  |  | 6:00 to 12:00: 21; else: 19
|  |  | 0.5 |  | CZ8 | 6:00 to 23:00: 22; else: 23 |  |  | 6:00 to 12:00: 21; else: 19
|  |  | 1.1 | Australian Building Code | CZ1, 2, 3 | 6 to 23h: 26; else: 23 | RMOT*0.26+15.9+3.45 | 6 to 23h: 26; else: 23 | 6 to 12am: 21; else: 19 | RMOT*0.26+15.9-3.45 | 6 to 12am: 21; else: 19
|  |  | 1.2 | Australian Building Code | CZ4 | 6 to 23h: 25; else: 23 | RMOT*0.26+15.9+3.45 | 6 to 23h: 25; else: 23 | 6 to 12am: 21; else: 19 | RMOT*0.26+15.9-3.45 | 6 to 12am: 21; else: 19
|  |  | 1.3 | Australian Building Code | CZ5 | 6 to 23h: 24; else: 23 | RMOT*0.26+15.9+3.45 | 6 to 23h: 24; else: 23 | 6 to 12am: 21; else: 19 | RMOT*0.26+15.9-3.45 | 6 to 12am: 21; else: 19
|  |  | 1.4 | Australian Building Code | CZ6, 7 | 6 to 23h: 23; else: 23 | RMOT*0.26+15.9+3.45 | 6 to 23h: 23; else: 23 | 6 to 12am: 21; else: 19 | RMOT*0.26+15.9-3.45 | 6 to 12am: 21; else: 19
|  |  | 1.5 | Australian Building Code | CZ8 | 6 to 23h: 22; else: 23 | RMOT*0.26+15.9+3.45 | 6 to 23h: 22; else: 23 | 6 to 12am: 21; else: 19 | RMOT*0.26+15.9-3.45 | 6 to 12am: 21; else: 19
|  |  | 2 | ISO 7730 | All | 24 | RMOT*0.26+15.9+3.45 | 26 | 20 | RMOT*0.26+15.9-3.45 | 23
|  |  | 3 | Adap. Limits Horizont. Extended | All | 10*0.26+15.9+3.45 | RMOT*0.26+15.9+3.45 | 25*0.26+15.9+3.45 | 10*0.26+15.9-3.45 | RMOT*0.26+15.9-3.45 | 25*0.26+15.9-3.45
14 | AUS DeDear | 80 | 0.1 |  | CZ1, 2, 3 | 6:00 to 23:00: 27; else: 24 |  |  | 6:00 to 12:00: 20; else: 18
|  |  | 0.2 |  | CZ4 | 6:00 to 23:00: 26; else: 24 |  |  | 6:00 to 12:00: 20; else: 18
|  |  | 0.3 |  | CZ5 | 6:00 to 23:00: 25; else: 24 |  |  | 6:00 to 12:00: 20; else: 18
|  |  | 0.4 |  | CZ6, 7 | 6:00 to 23:00: 24; else: 24 |  |  | 6:00 to 12:00: 20; else: 18
|  |  | 0.5 |  | CZ8 | 6:00 to 23:00: 23; else: 24 |  |  | 6:00 to 12:00: 20; else: 18
|  |  | 1.1 | Australian Building Code | CZ1, 2, 3 | 6 to 23h: 27; else: 24 | PMOT*0.26+16.75+4.5 | 6 to 23h: 27; else: 24 | 6 to 12am: 20; else: 18 | PMOT*0.26+16.75-4.5 | 6 to 12am: 20; else: 18
|  |  | 1.2 | Australian Building Code | CZ4 | 6 to 23h: 26; else: 24 | PMOT*0.26+16.75+4.5 | 6 to 23h: 26; else: 24 | 6 to 12am: 20; else: 18 | PMOT*0.26+16.75-4.5 | 6 to 12am: 20; else: 18
|  |  | 1.3 | Australian Building Code | CZ5 | 6 to 23h: 25; else: 24 | PMOT*0.26+16.75+4.5 | 6 to 23h: 25; else: 24 | 6 to 12am: 20; else: 18 | PMOT*0.26+16.75-4.5 | 6 to 12am: 20; else: 18
|  |  | 1.4 | Australian Building Code | CZ6, 7 | 6 to 23h: 24; else: 24 | PMOT*0.26+16.75+4.5 | 6 to 23h: 24; else: 24 | 6 to 12am: 20; else: 18 | PMOT*0.26+16.75-4.5 | 6 to 12am: 20; else: 18
|  |  | 1.5 | Australian Building Code | CZ8 | 6 to 23h: 23; else: 24 | PMOT*0.26+16.75+4.5 | 6 to 23h: 23; else: 24 | 6 to 12am: 20; else: 18 | PMOT*0.26+16.75-4.5 | 6 to 12am: 20; else: 18
|  |  | 2 | ISO 7730 | All | 25 | PMOT*0.26+16.75+4.5 | 27 | 19 | PMOT*0.26+16.75-4.5 | 22
|  |  | 3 | Adap. Limits Horizont. Extended | All | 8*0.26+16.75+4.5 | PMOT*0.26+16.75+4.5 | 27*0.26+16.75+4.5 | 8*0.26+16.75-4.5 | PMOT*0.26+16.75-4.5 | 27*0.26+16.75-4.5
|  | 90 | 0.1 |  | CZ1, 2, 3 | 6:00 to 23:00: 26; else: 23 |  |  | 6:00 to 12:00: 21; else: 19
|  |  | 0.2 |  | CZ4 | 6:00 to 23:00: 25; else: 23 |  |  | 6:00 to 12:00: 21; else: 19
|  |  | 0.3 |  | CZ5 | 6:00 to 23:00: 24; else: 23 |  |  | 6:00 to 12:00: 21; else: 19
|  |  | 0.4 |  | CZ6, 7 | 6:00 to 23:00: 23; else: 23 |  |  | 6:00 to 12:00: 21; else: 19
|  |  | 0.5 |  | CZ8 | 6:00 to 23:00: 22; else: 23 |  |  | 6:00 to 12:00: 21; else: 19
|  |  | 1.1 | Australian Building Code | CZ1, 2, 3 | 6 to 23h: 26; else: 23 | PMOT*0.26+16.75+3.5 | 6 to 23h: 26; else: 23 | 6 to 12am: 21; else: 19 | PMOT*0.26+16.75-3.5 | 6 to 12am: 21; else: 19
|  |  | 1.2 | Australian Building Code | CZ4 | 6 to 23h: 25; else: 23 | PMOT*0.26+16.75+3.5 | 6 to 23h: 25; else: 23 | 6 to 12am: 21; else: 19 | PMOT*0.26+16.75-3.5 | 6 to 12am: 21; else: 19
|  |  | 1.3 | Australian Building Code | CZ5 | 6 to 23h: 24; else: 23 | PMOT*0.26+16.75+3.5 | 6 to 23h: 24; else: 23 | 6 to 12am: 21; else: 19 | PMOT*0.26+16.75-3.5 | 6 to 12am: 21; else: 19
|  |  | 1.4 | Australian Building Code | CZ6, 7 | 6 to 23h: 23; else: 23 | PMOT*0.26+16.75+3.5 | 6 to 23h: 23; else: 23 | 6 to 12am: 21; else: 19 | PMOT*0.26+16.75-3.5 | 6 to 12am: 21; else: 19
|  |  | 1.5 | Australian Building Code | CZ8 | 6 to 23h: 22; else: 23 | PMOT*0.26+16.75+3.5 | 6 to 23h: 22; else: 23 | 6 to 12am: 21; else: 19 | PMOT*0.26+16.75-3.5 | 6 to 12am: 21; else: 19
|  |  | 2 | ISO 7730 | All | 24 | PMOT*0.26+16.75+3.5 | 26 | 20 | PMOT*0.26+16.75-3.5 | 23
|  |  | 3 | Adap. Limits Horizont. Extended | All | 8*0.26+16.75+3.5 | PMOT*0.26+16.75+3.5 | 27*0.26+16.75+3.5 | 8*0.26+16.75-3.5 | PMOT*0.26+16.75-3.5 | 27*0.26+16.75-3.5
15 | BRA Rupp NV | 80 | 0 |  | WS | 23.5 |  |  | 21
[5 empty] | SS | 25.5 |  |  | 22.5
|  |  | 1 | ABNT NBR 16401-2 Standard | All | 23.5 | PMOT*0.56+12.74+3.8 | 25.5 | 21 | PMOT*0.56+12.74-3.8 | 22.5
|  |  | 2 | ISO 7730 | All | 25 | PMOT*0.56+12.74+3.8 | 27 | 19 | PMOT*0.56+12.74-3.8 | 22
|  |  | 3 | Adap. Limits Horizont. Extended | All | 16.9*0.56+12.74+3.8 | PMOT*0.56+12.74+3.8 | 24.8*0.56+12.74+3.8 | 16.9*0.56+12.74-3.8 | PMOT*0.56+12.74-3.8 | 24.8*0.56+12.74-3.8
|  | 90 | 0 |  | WS | 23 |  |  | 21.5
[5 empty] | SS | 25 |  |  | 23
|  |  | 1 | ABNT NBR 16401-2 Standard | All | 23 | PMOT*0.56+12.74+2.8 | 25 | 21.5 | PMOT*0.56+12.74-2.8 | 23
|  |  | 2 | ISO 7730 | All | 24 | PMOT*0.56+12.74+2.8 | 26 | 20 | PMOT*0.56+12.74-2.8 | 23
|  |  | 3 | Adap. Limits Horizont. Extended | All | 16.9*0.56+12.74+2.8 | PMOT*0.56+12.74+2.8 | 24.8*0.56+12.74+2.8 | 16.9*0.56+12.74-2.8 | PMOT*0.56+12.74-2.8 | 24.8*0.56+12.74-2.8
16 | BRA Rupp AC | 80 | 0 |  | WS | 23.5 |  |  | 21
[5 empty] | SS | 25.5 |  |  | 22.5
|  |  | 1 | ABNT NBR 16401-2 Standard | All | 23.5 | PMOT*0.09+22.32+2.1 | 25.5 | 21 | PMOT*0.09+22.32-2.1 | 22.5
|  |  | 2 | ISO 7730 | All | 25 | PMOT*0.09+22.32+2.1 | 27 | 19 | PMOT*0.09+22.32-2.1 | 22
|  |  | 3 | Limits Horizont. Extended | All | 16.4*0.09+22.32+2.1 | PMOT*0.09+22.32+2.1 | 25.7*0.09+22.32+2.1 | 16.4*0.09+22.32-2.1 | PMOT*0.09+22.32-2.1 | 25.7*0.09+22.32-2.1
|  | 90 | 0 |  | WS | 23 |  |  | 21.5
[5 empty] | SS | 25 |  |  | 23
|  |  | 1 | ABNT NBR 16401-2 Standard | All | 25 | PMOT*0.09+22.32+1.1 | 25 | 23 | PMOT*0.09+22.32-1.1 | 23
|  |  | 2 | ISO 7730 | All | 24 | PMOT*0.09+22.32+1.1 | 26 | 20 | PMOT*0.09+22.32-1.1 | 23
|  |  | 3 | Limits Horizont. Extended | All | 16.4*0.09+22.32+1.1 | PMOT*0.09+22.32+1.1 | 25.7*0.09+22.32+1.1 | 16.4*0.09+22.32-1.1 | PMOT*0.09+22.32-1.1 | 25.7*0.09+22.32-1.1
17 | MEX Oropeza Arid | 80 | 0 |  | All | 25 |  |  | 20
|  |  | 1 | Relevant static setpoints for Mex | WS | 25 | PMOT*0.48+13.9+3 | 25 | 20 | PMOT*0.48+13.9-3 | 20
[5 empty] | SS | 25 | PMOT*0.59+9.6+3 | 25 | 20 | PMOT*0.59+9.6-3 | 20
|  |  | 2 | ISO 7730 | WS | 27 | PMOT*0.48+13.9+3 | 25 | 19 | PMOT*0.48+13.9-3 | 22
[5 empty] | SS | 27 | PMOT*0.59+9.6+3 | 25 | 19 | PMOT*0.59+9.6-3 | 22
|  |  | 3 | Adap. Limits Horizont. Extended | WS | 11.25*0.48+13.9+3 | PMOT*0.48+13.9+3 | 25.25*0.48+13.9+3 | 11.25*0.48+13.9-3 | PMOT*0.48+13.9-3 | 25.25*0.48+13.9-3
[5 empty] | SS | 23*0.59+9.6+3 | PMOT*0.59+9.6+3 | 45*0.59+9.6+3 | 23*0.59+9.6-3 | PMOT*0.59+9.6-3 | 45*0.59+9.6-3
|  | 90 | 0 |  | All | 25 |  |  | 20
|  |  | 1 | Relevant static setpoints for Mex | WS | 25 | PMOT*0.48+13.9+2 | 25 | 20 | PMOT*0.48+13.9-2 | 20
[5 empty] | SS | 25 | PMOT*0.59+9.6+2 | 25 | 20 | PMOT*0.59+9.6-2 | 20
|  |  | 2 | ISO 7730 | WS | 26 | PMOT*0.48+13.9+2 | 24 | 20 | PMOT*0.48+13.9-2 | 23
[5 empty] | SS | 26 | PMOT*0.59+9.6+2 | 24 | 20 | PMOT*0.59+9.6-2 | 23
|  |  | 3 | Adap. Limits Horizont. Extended | WS | 11.25*0.48+13.9+2 | PMOT*0.48+13.9+2 | 25.25*0.48+13.9+2 | 11.25*0.48+13.9-2 | PMOT*0.48+13.9-2 | 25.25*0.48+13.9-2
[5 empty] | SS | 23*0.59+9.6+2 | PMOT*0.59+9.6+2 | 45*0.59+9.6+2 | 23*0.59+9.6-2 | PMOT*0.59+9.6-2 | 45*0.59+9.6-2
18 | MEX Oropeza DryTropic | 80 | 0 |  | All | 25 |  |  | 20
|  |  | 1 | Relevant static setpoints for Mex | WS | 25 | PMOT*0.84+5.3+3 | 25 | 20 | PMOT*0.84+5.3-3 | 20
[5 empty] | SS | 25 | PMOT*0.96-3.6+3 | 25 | 20 | PMOT*0.96-3.6-3 | 20
|  |  | 2 | ISO 7730 | WS | 27 | PMOT*0.84+5.3+3 | 25 | 19 | PMOT*0.84+5.3-3 | 22
[5 empty] | SS | 27 | PMOT*0.96-3.6+3 | 25 | 19 | PMOT*0.96-3.6-3 | 22
|  |  | 3 | Adap. Limits Horizont. Extended | WS | 15.5*0.84+5.3+3 | PMOT*0.84+5.3+3 | 27.5*0.84+5.3+3 | 15.5*0.84+5.3-3 | PMOT*0.84+5.3-3 | 27.5*0.84+5.3-3
[5 empty] | SS | 23*0.96-3.6+3 | PMOT*0.96-3.6+3 | 34*0.96-3.6+3 | 23*0.96-3.6-3 | PMOT*0.96-3.6-3 | 34*0.96-3.6-3
|  | 90 | 0 |  | All | 25 |  |  | 20
|  |  | 1 | Relevant static setpoints for Mex | WS | 25 | PMOT*0.84+5.3+2 | 25 | 20 | PMOT*0.84+5.3-2 | 20
[5 empty] | SS | 25 | PMOT*0.96-3.6+2 | 25 | 20 | PMOT*0.96-3.6-2 | 20
|  |  | 2 | ISO 7730 | WS | 26 | PMOT*0.84+5.3+2 | 24 | 20 | PMOT*0.84+5.3-2 | 23
[5 empty] | SS | 26 | PMOT*0.96-3.6+2 | 24 | 20 | PMOT*0.96-3.6-2 | 23
|  |  | 3 | Adap. Limits Horizont. Extended | WS | 15.5*0.84+5.3+2 | PMOT*0.84+5.3+2 | 27.5*0.84+5.3+2 | 15.5*0.84+5.3-2 | PMOT*0.84+5.3-2 | 27.5*0.84+5.3-2
[5 empty] | SS | 23*0.96-3.6+2 | PMOT*0.96-3.6+2 | 34*0.96-3.6+2 | 23*0.96-3.6-2 | PMOT*0.96-3.6-2 | 34*0.96-3.6-2
19 | MEX Oropeza Temperate | 80 | 0 |  | All | 25 |  |  | 20
|  |  | 1 | Relevant static setpoints for Mex | WS | 25 | PMOT*0.27+17.9+2 | 25 | 20 | PMOT*0.27+17.9-2 | 20
[5 empty] | SS | 25 | PMOT*0.53+10.3+1 | 25 | 20 | PMOT*0.53+10.3-1 | 20
|  |  | 2 | ISO 7730 | WS | 27 | PMOT*0.27+17.9+2 | 25 | 19 | PMOT*0.27+17.9-2 | 22
[5 empty] | SS | 27 | PMOT*0.53+10.3+1 | 25 | 19 | PMOT*0.53+10.3-1 | 22
|  |  | 3 | Adap. Limits Horizont. Extended | WS | 5*0.27+17.9+2 | PMOT*0.27+17.9+2 | 25.25*0.27+17.9+2 | 5*0.27+17.9-2 | PMOT*0.27+17.9-2 | 25.25*0.27+17.9-2
[5 empty] | SS | 11.75*0.53+10.3+1 | PMOT*0.53+10.3+1 | 25.25*0.53+10.3+1 | 11.75*0.53+10.3-1 | PMOT*0.53+10.3-1 | 25.25*0.53+10.3-1
|  | 90 | 0 |  | All | 25 |  |  | 20
|  |  | 1 | Relevant static setpoints for Mex | WS | 25 | PMOT*0.27+17.9+3 | 25 | 20 | PMOT*0.27+17.9-3 | 20
[5 empty] | SS | 25 | PMOT*0.53+10.3+2 | 25 | 20 | PMOT*0.53+10.3-2 | 20
|  |  | 2 | ISO 7730 | WS | 26 | PMOT*0.27+17.9+3 | 24 | 20 | PMOT*0.27+17.9-3 | 23
[5 empty] | SS | 26 | PMOT*0.53+10.3+2 | 24 | 20 | PMOT*0.53+10.3-2 | 23
|  |  | 3 | Adap. Limits Horizont. Extended | WS | 5*0.27+17.9+3 | PMOT*0.27+17.9+3 | 25.25*0.27+17.9+3 | 5*0.27+17.9-3 | PMOT*0.27+17.9-3 | 25.25*0.27+17.9-3
[5 empty] | SS | 11.75*0.53+10.3+2 | PMOT*0.53+10.3+2 | 25.25*0.53+10.3+2 | 11.75*0.53+10.3-2 | PMOT*0.53+10.3-2 | 25.25*0.53+10.3-2
20 | MEX Oropeza HumTropic | 80 | 0 |  | All | 25 |  |  | 20
|  |  | 1 | Relevant static setpoints for Mex | WS | 25 | PMOT*0.38+15.7+2 | 25 | 20 | PMOT*0.38+15.7-2 | 20
[5 empty] | SS | 25 | PMOT*0.47+9.07+5 | 25 | 20 | PMOT*0.47+9.07-5 | 20
|  |  | 2 | ISO 7730 | WS | 27 | PMOT*0.38+15.7+2 | 25 | 19 | PMOT*0.38+15.7-2 | 22
[5 empty] | SS | 27 | PMOT*0.47+9.07+5 | 25 | 19 | PMOT*0.47+9.07-5 | 22
|  |  | 3 | Adap. Limits Horizont. Extended | WS | 13*0.38+15.7+2 | PMOT*0.38+15.7+2 | 29.75*0.38+15.7+2 | 13*0.38+15.7-2 | PMOT*0.38+15.7-2 | 29.75*0.38+15.7-2
[5 empty] | SS | 23*0.47+9.07+5 | PMOT*0.47+9.07+5 | 45*0.47+9.07+5 | 23*0.47+9.07-5 | PMOT*0.47+9.07-5 | 45*0.47+9.07-5
|  | 90 | 0 |  | All | 25 |  |  | 20
|  |  | 1 | Relevant static setpoints for Mex | WS | 25 | PMOT*0.38+15.7+3 | 25 | 20 | PMOT*0.38+15.7-3 | 20
[5 empty] | SS | 25 | PMOT*0.47+9.07+6 | 25 | 20 | PMOT*0.47+9.07-6 | 20
|  |  | 2 | ISO 7730 | WS | 26 | PMOT*0.38+15.7+3 | 24 | 20 | PMOT*0.38+15.7-3 | 23
[5 empty] | SS | 26 | PMOT*0.47+9.07+6 | 24 | 20 | PMOT*0.47+9.07-6 | 23
|  |  | 3 | Adap. Limits Horizont. Extended | WS | 13*0.38+15.7+3 | PMOT*0.38+15.7+3 | 29.75*0.38+15.7+3 | 13*0.38+15.7-3 | PMOT*0.38+15.7-3 | 29.75*0.38+15.7-3
[5 empty] | SS | 23*0.47+9.07+6 | PMOT*0.47+9.07+6 | 45*0.47+9.07+6 | 23*0.47+9.07-6 | PMOT*0.47+9.07-6 | 45*0.47+9.07-6
21 | CHL Perez-Fargallo | 80 | 0 | ? | All | ? |  |  | ?
|  |  | 1 | ? | All | ? | ? | ? | ? | ? | ?
|  |  | 2 | ISO 7730 | All | 25 | PMOT*0.678+13.51+4 | 27 | 19 | PMOT*0.678+13.51-4 | 22
|  |  | 3 | Adap. Limits Horizont. Extended | All | 6.5*0.678+13.51+4 | PMOT*0.678+13.51+4 | 20*0.678+13.51+4 | 6.5*0.678+13.51-4 | PMOT*0.678+13.51-4 | 20*0.678+13.51-4
|  | 90 | 0 | ? | All | ? |  |  | ?
|  |  | 1 | ? | All | ? | ? | ? | ? | ? | ?
|  |  | 2 | ISO 7730 | All | 24 | PMOT*0.678+13.51+2.5 | 26 | 20 | PMOT*0.678+13.51-2.5 | 23
|  |  | 3 | Adap. Limits Horizont. Extended | All | 6.5*0.678+13.51+2.5 | PMOT*0.678+13.51+2.5 | 20*0.678+13.51+2.5 | 6.5*0.678+13.51-2.5 | PMOT*0.678+13.51-2.5 | 20*0.678+13.51-2.5
22 | INT ISO7730 | 1: A | 0 | - | WS | 23 |  |  | 21
|  |  |  | - | SS | 25.5 |  |  | 23.5
|  | 2: B | 0 | - | WS | 24 |  |  | 20
|  |  |  | - | SS | 26 |  |  | 23
|  | 3: C | 0 | - | WS | 25 |  |  | 19
|  |  |  | - | SS | 27 |  |  | 22
PMOT: Prevailing mean outdoor temperature; RMOT: Running mean outdoor temperature; WS: Winter season; SS: Summer season; NA: Not applicable;
ACSTall: Adaptive Cooling Setpoint Temperature applicability lower limit; ACSTaul: Adaptive Cooling Setpoint Temperature applicability upper limit;
AHSTall: Adaptive Heating Setpoint Temperature applicability lower limit; AHSTaul: Adaptive Heating Setpoint Temperature applicability upper limit;
WMOT: Weighted Mean Outdoor Temperature (can be either RMOT or PMOT)
?: Functions to be added